## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST E-TENDER NO. 54/EUDC-I/2023-24/NOIDA (WORKS) FOR CARRYING OUT THE 32 NOS. WORK WORK CONSTRUCTION OF 11/0.4 KV S/S IN AREA OF EUDSD-I/IV, NOIDA UNDER EUDD-I, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA (SYSTEM STRENGTHENING WORKS IN MUNICIPAL AREA INCLUDING NOIDA RS. 72.00 CRORE FOR NOIDA ZONE).
Contact No: 0120-2970431
The bidder quoted rate should be inclusive GST & all other taxes.
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. The bidder quoted rate should be inclusive GST & all other taxes. 2. Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC. 3. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder with GST & all other taxes Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | FOLLOWING 32 NOS. WORK CONSTRUCTION OF 11/0.4 KV S/S AT VARIOUS PLACES IN AREA OF EUDSD-I/IV, NOIDA :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | Cartage of ST poles 11 mtr long from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Nos. | 100 |  |  | Excess(+) | 75 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Cartage of ST poles 13 mtr long from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | Cartage of PCC poles 8.5 / 9 mtr long from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Nos. | 100 |  |  | Excess(+) | 74 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | Cartage of other line material such as 11KV Disc Insulator T&C Type 4500 kg. with Fitting (204 Nos.), 11 KV Pin Insulator with Pin, nut & bolts (333 Nos.) etc. from ESC Noida/Sahibabad/Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Cartage of ACSR Dog Conductor from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 4020 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | Cartage of LT ABC 3x120+1x95+1x16 (8603 Mtrs.) & 3x120+1x95+1x35 (240 Mtrs.) Sq.mm. from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 8843 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.07 | Cartage of LT XLPE Cable 1x35 Sq.mm. (1582 Mtrs.) & LT XLPE Cable 3.5x400 Sq.mm. (160 Mtrs.) from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 1742 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.08 | Cartage of HT XLPE Cable 3x120 Sq.mm. from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 460 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.09 | The Excavation of foundation pit in CC road/ mix soil/ normal soil/ soft & hard rack by using heavy duty compressor and its back filling and leveling etc. The size of the pit will be 600x600x1800 mm for each pole and having a depth of 1/6 of the full length of the support. |  | 1 | Nos. | 100 |  |  | Excess(+) | 161 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | Erection of Double Pole on 11 Mtr. long ST Pole for LT line including fixing of all accessories of LT line as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.11 | Erection of Pole on 11 Mtr. long ST Pole for LT line including fixing of all accessories of LT line as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 9 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.12 | Erection of Pole on 13 Mtr. long ST Pole for LT line including fixing of all accessories of LT line as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.13 | Erection of Pole on 8.5 / 9 Mtr. long PCC Pole for LT line including fixing of all accessories of LT line as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 74 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.14 | Grouting of each pole (In ratio of 1:4:8 in Cement, sand and Brick Ballast) in size 450mmx450mmx1800 mm as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 161 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.15 | Construction of Plinth in size 450x450x300 mm of each (0.880 Cu.m.each) pole above the ground level (In ratio of 1:3:6 in Cement, sand and Brick Ballast) as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 87 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.16 | Laying, Lifting and final Binding, Sagging of ACSR Dog Conductor including fixing of all accessories as per RESPO schedule Complete in all respects. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 4020 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.17 | Laying, Lifting and final Binding, Sagging of LT ABC LT ABC 3x120+1x95+1x16 (8603 Mtrs.) & 3x120+1x95+1x35 (240 Mtrs.) Sq.mm. including fixing of all accessories as per RESPO schedule Complete in all respects. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 8843 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.18 | PROVIDING & FABRICATION / FIXING OF FOLLOWING MATERIAL OF BEST QUALITY FOR COMPLETION OF WORK AS PER SITE REQUIREMENT :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.19 | 11 KV TPMO |  | 1 | Nos. | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.2 | 11 KV Fuse set |  | 1 | Nos. | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.21 | LT PVC Cable Al. 3.5x240 Sq.mm. (40 Mtrs.) & 3.5x400 Sq.mm. (1320 Mtrs.) (Laying of Cable including fixing of all accessories as per RESPO schedule Complete in all respects.) |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 1360 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.22 | LT PVC Cable Al. 1x400 Sq.mm. (80 Mtrs.) & 1x630 Sq.mm. (2480 Mtrs.) (Laying of Cable including fixing of all accessories as per RESPO schedule Complete in all respects.) |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 2560 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.23 | Stay set 16x1800 mm (Grouting & Concreting of stay rod 1800x16 mm complete in all respect as per RESPO schedule Complete in all respects.), (Fixing, Tighting and nozzling of stay wire 5 kg with the pole of required tension with clamps, bolt & nut as per RESPO schedule Complete in all respects.) |  | 1 | Nos. | 100 |  |  | Excess(+) | 62 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.24 | MS Earthing Rod (2540x20 mm) complete (Excavation of earth and driving of M.S. earthing rod of size 20x2540 mm in earth and jointing through G.I wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts etc. as per RESPO schedule Complete in all respects.) |  | 1 | Nos. | 100 |  |  | Excess(+) | 68 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.25 | Top channel 125x65x2240mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 65 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.26 | Dropper channel 100x50x2028mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 61 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.27 | MS channel for Fuse set 100x50x2028mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 65 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.28 | MS T-off channel |  | 1 | Nos. | 100 |  |  | Excess(+) | 64 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.29 | MS channel 125x65x1300mm (T-off) |  | 1 | Nos. | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.3 | MS Holding Clamp with bolt and nuts. |  | 1 | Nos. | 100 |  |  | Excess(+) | 394 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.31 | Al. Crimping Lug 400 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 528 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.32 | Al. Crimping Lug 240 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 264 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.33 | Stone Pad 300x300x75mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 69 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.34 | ST Pole Clamp |  | 1 | Nos. | 100 |  |  | Excess(+) | 528 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.35 | Suspension Clamp with I-Hook |  | 1 | Nos. | 100 |  |  | Excess(+) | 469 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.36 | Dead End Clamp with I-Hook |  | 1 | Nos. | 100 |  |  | Excess(+) | 134 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.37 | LT Piercing connector |  | 1 | Nos. | 100 |  |  | Excess(+) | 516 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.38 | LT Distribution Box 3 Phase |  | 1 | Nos. | 100 |  |  | Excess(+) | 254 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.39 | Clamp for Distribution box with nut & bolt |  | 1 | Nos. | 100 |  |  | Excess(+) | 254 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.4 | Al. lug long barrel |  | 1 | Nos. | 100 |  |  | Excess(+) | 496 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.41 | PCC pole Clamp |  | 1 | Nos. | 100 |  |  | Excess(+) | 194 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.42 | Construction of new distribution 400 KVA T/F (32 Nos.) & 250 KVA T/F (1 No.) Plinth. The size of plinth shall be 2 Mtrs. long, 2 Mtrs. wide and height 1.5 Mtrs. from ground level with 15 CM thick top CC slab. The above work includes Excavation of earth, laying of bring ballast pad for foundation brick work, CC and plastering and proper curing complete with all respects as per RESPO schedule. |  | 1 | Nos. | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.43 | Safe loading and carriage of 400 KVA (32 Nos.) & 250 KVA T/F (01 No.) Transformer from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends |  | 1 | Nos. | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.44 | Mounting, installation of 400 KVA (32 Nos.) & 250 KVA T/F (01 No.) Transformer on above Plinth, alongwith double earthing of the same, complete in all respect as per RESPO schedule. |  | 1 | Nos. | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.45 | Providing and installation of LT ACB 630 Amp. with cabinet / structure (Make L&T, Schneider, ABB, Hevell's) as per following specification with all relevant certificate :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.46 | 630 amp. 03 pole fixed manual ACB. |  | 1 | Nos. | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.47 | Red/yellow/blue light indication |  | 1 | Sets | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.48 | ON & OFF Indication |  | 1 | Nos. | 100 |  |  | Excess(+) | 132 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.49 | Amp., Volt meter& energy meter digital |  | 1 | Nos. | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.5 | Metering C.T 630/5A, |  | 1 | Nos. | 100 |  |  | Excess(+) | 198 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.51 | Panel fabrication of size 1250mm x 900mm x 600 mm made of M.S sheet 14 gauge with powder coating with panel lock and key arrangement.(two nos). and additional locking arrangement seprately including providing hut type shape as per drg. |  | 1 | Nos. | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.52 | Fabrication of aluminium bus-bar for each phases | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.53 | Incoming size 425 mm x 50mmx12 mm (twin) |  | 1 | Nos. | 100 |  |  | Excess(+) | 528 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.54 | Out going size 720 mm x 50mm x 12 mm(twin) |  | 1 | Nos. | 100 |  |  | Excess(+) | 528 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.55 | Neutral size 900mmx50mmx12 mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.56 | Fabrication of pannel stand made of M.S Angle of size 900mm x 600mm x 500 mm as per drg. |  | 1 | Nos. | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.57 | Assembly of above ACB, Indicators, Meters, Metering CT & bus bar arrangment in the panel, fitting the panel on Stand with nut and bolts with wiring etc. & grouting in ratio 1:4:8 with cement, coarse sand and brick blast. |  | 1 | Jobs | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.58 | Providing and fixing of aluminium bus bar of size 300mmx60mmx12 mm on L.T side of T/F. |  | 1 | Nos. | 100 |  |  | Excess(+) | 528 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.59 | Making all connections with ACB & Distribution T/F and commissioning the ACB complete in all respect. |  | 1 | Jobs | 100 |  |  | Excess(+) | 66 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.6 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR 400 / 250 KVA TRANSFORMERS (BODY & NEUTRAL) AND ACB (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.61 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 50 mm length 3 mtr - 32mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for 400 / 250 KVA distribution t/f & ACB installed at Above 11/0.4 KV L.T. Substation. |  | 1 | Nos. | 100 |  |  | Excess(+) | 132 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.62 | Providing and fixing of GI strip of size 32 mm x 6 mm suitable for 400 / 250 KVA distribution t/f & ACB installed at Above 11/0.4 KV L.T. Substation. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 396 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.63 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 396 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.64 | WORK OF PROVIDING AND FIXING OF 33 NOS. NEW WIREMESH FENCING OF 11/0.4 KV L.T. SUB-STATION INSTALLED AT ABOVE PLACE AS PER FOLLOWING :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.65 | Providing & Fixing of new WIREMESH fencing frames of size 12'X15'x6' for each fencing of LT Sub-stations.) (All Material provided by contractor for above work.) |  | 1 | Jobs | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.66 | Construction of boundry / toe wall in bottom of fencing in brick work cement mortar 1:6 (1 cement : 6 coarse sand) for link in the size of 0.22mx0.60m (0.30m in earth, 0.30m above ground level) including plaster in cement mortar 1:4 and finishing with water proof cement paint. (Approx construction 12 Mtrs. boundry / toe wall for each fencing of LT Sub-stations.) (All Material provided by contractor for above work) |  | 1 | Jobs | 100 |  |  | Excess(+) | 33 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.67 | Laying of LT XLPE Cable 1x35 Sq.mm. in trench and as per work site requirement including fixing of all accessories Complete in all respects. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 1582 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.68 | Drilling of dia 160 mm in single bore by trench less method by horizontal boring machine at a depth of 1.5 mtrs below the ground level complete in all respects. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 360 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.69 | Providing of 06 Mtr long pieces of HDPE pipe 6 Inch Dia PN 4 PE 63 (PVVNL approved) after inspection of competent committee at manufacturing site of the items with actual guarantee period. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 360 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.7 | Laying and interconnecting of above 06 Mtr long pieces of HDPE pipe 6 inch Dia PN 4 PE 63 (PVVNL approved). |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 360 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.71 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop. |  | 1 | Jobs | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.72 | Providing of HDPE Socket suitable for HDPE pipe 6 inch dia. |  | 1 | Nos. | 100 |  |  | Excess(+) | 60 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.73 | Fixing of above HDPE Socket LT / HT XLPE Cable and 6 inch dia pipe. |  | 1 | Nos. | 100 |  |  | Excess(+) | 60 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.74 | Road Restoration charges for hot mixed pakka road / CC road/ mix soil/ normal soil/ soft & hard rack as it is when start of work as per authority norms. |  | 1 | Jobs | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.75 | Laying and pulling of LT XLPE Cable 3.5x400 Sq.mm. & HT XLPE Cable 3x120 Sq.mm. Cable through HDPE pipe and loop. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 620 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.76 | Providing of Outdoor / Indoor / Straight Through jointing kit of Raychem/ 3M/ Denson make suitable for Above LT XLPE Cable |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.77 | Fixing of above Outdoor / Indoor / Straight Through jointing kit of Raychem/ 3M/ Denson make suitable for Above LT XLPE Cable |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.78 | Hi port test for T XLPE Cable 3.5x400 Sq.mm. & HT XLPE Cable 3x120 Sq.mm. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 620 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information