## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST E-TENDER NO. 63/EUDC-I/2023-24/NOIDA (WORKS) FOR CARRYING OUT THE 01 NOS. WORK INSTALLATION OF RMUs IN ALL FEEDERS OF S/S SECTOR-32 NOIDA AREA SECTOR-32, 33 & 34 NOIDA IN THE AREA OF EUDSD-II, NOIDA UNDER EUDD-VII, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA (SYSTEM STRENGTHENING WORKS IN MUNICIPAL AREA INCLUDING NOIDA RS. 72.00 CRORE FOR NOIDA ZONE).
Contact No: 0120-2970431
The bidder quoted rate should be inclusive GST & all other taxes.
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. The bidder quoted rate should be inclusive GST & all other taxes. 2. Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC. 3. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder with GST & all other taxes Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | WORK SUPPLY AND INSTALLATION OF RMUs IN ALL FEEDERS OF S/S SECTOR-32 NOIDA AREA SECTOR-32, 33 & 34 NOIDA IN THE AREA OF EUDSD-II, NOIDA AS PER FOLLOWING SPECIFICATION AND ATTACHED APPROVED G.T.P. :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 3-way, fully motorised and manually operated Ring main unit (2 LBS & 1 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits. . All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . .Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 9 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 3-way, fully motorised and manually operated Ring main unit (3 LBS) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits. . All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . .Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 4-way,fully motorised and manually operated Ring main unit ( 2 LBS & 2 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot termination Kits. All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . .Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 4-way,fully motorised and manually operated Ring main unit ( 3 LBS & 1 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot termination Kits. All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . .Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 5-way,fully motorised and manually operated Ring main unit ( 3 LBS & 2 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot termination Kits. . All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . .Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 5-way,fully motorised and manually operated Ring main unit ( 2 LBS & 3 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot termination Kits. . All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . .Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.07 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 6-way,fully motorised and manually operated Ring main unit ( 4 LBS & 2 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot termination Kits. . All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.08 | 12kV 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 6-way,fully motorised and manually operated Ring main unit ( 3 LBS & 3 VCB) consisting of copper busbar in SF6 insulated. RMU should be type tested for internal arc of 21 KA for 1 Sec. for Gas tank and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel .Suitable CT 100-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot termination Kits. . All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope) . Aux. PT Battery, Charger etc. for Motorised operation of RMU to be provided. The scope is including Plinth/Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 1000 Mtrs above Sea Level. ( Makes: ABB / Siemens / Eaton / Schneider). |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.09 | Construction of Plinth of size 6'x3'x3' (LxWxH) for above RMUs complete in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR ABOVE RMUs (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.11 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 50 mm length 3 mtr - 32mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for RMUsF installed at Above 33/11 KV Substation . |  | 1 | Nos. | 100 |  |  | Excess(+) | 56 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.12 | Providing and fixing of GI strip of size 32 mm x 6 mm suitable for RMUs installed at Above 33/11 KV Substation . |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 168 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.13 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 168 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.14 | Providing of 01 No. Technical person (knowledge about RMUs operation) for technical support for smooth operation of above RMUs in warranty period. |  | 1 | Month | 100 |  |  | Excess(+) | 60 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information