# PRE QUALIFYING CONDITIONS FOR SUPPLY OF METER

Tender's meeting the following conditions only will be considered.

- QUALIFICATION OF TENDERES:

(a)	The tenderers shall either themselves be manufacturers of the equipment offered or accredited representatives of such manufacturers in India or of their principals abroad with whom they may be having collaboration. Such accreditation should be at least of one year on date of tender.

(b)	Minimum Average Annual Turnover of Rs. 100 Crore for best three years out of last five financial years. However for UP based industries average turnover of Rs 50 Crore per year will be acceptable.

- The bidder must possess bureau of Indian Standard Certification (ISI Mark) and valid ISO 9001:2008 certification for meter manufacturing, ISO 27001:2005 for information security management system and ISO: 14001- 2004 for environmental management system.

- The bidder shall submit a copy of valid certificate of capability maturity model integration (CMMI) of minimum level 3 issued by recognized body like SEI etc along with his bid.

- Relevant documents in support of the above must be furnished along with bid. If these documents are not furnished along with the tenders, the price bid of the firm may not be opened, the offer will be liable to be rejected summarily.

- No trial Order shall be given.

2.	(a)	OPERATIONAL EXPERIENCES:

Offered equipment should have given three years proven trouble free operational service in tropical climate. However, in case of equipment being manufactured in India under valid FOREIGN COLLABORATION, operating experience in tropical climate of offered collaborator’s equipment shall also be acceptable provided copy of valid collaboration agreement for the equipment offered is submitted with the tender. Further, in case of offer of imported equipment, the three years operating experience will be considered in respect of those areas only which are similar to the tropical condition prevailing in India.

(b)	MANUFACTURING EXPERIENCE: The indigenous manufacturers or their foreign collaborator must have manufactured and supplied at least 100% of the quoted quantity to the Govt. power utility in India in last five years. The tenderer shall have to submit self attested copies of purchase orders & dispatch instructions receive for consignee and invoices etc. failing which their bid shall not be considered.

3.      	         TESTING FACILITIES:

The tenderer must have NABL accredited lab at their works for carrying out such routine and acceptance tests as prescribed in the relevant ISS, and IS 15959: 2011 and any other routine and acceptance test as specified in the specification. He should have all the facility in his work for design, assembly, quality assurance, burn-in test (fully assembled energy meter), testing (all routine and acceptance tests), automatic calibration of energy meter on software based test bench, qualified team of technical and software Engineers.  He should enclose documentary evidence of existence of such facilities along with tender bid, failing which price may not be opened.

4.      	         BLACK LISTING:

The Tender bids of those tenders who have been served with the notice for processing of “Black listing / debar” from any DISCOM of UPPCL or any PSU/Government Department/Financial Institution/Court shall not be considered. The bidder should submit an undertaking that they have not been suspended / blacklisted by any PSU/Government Department/Financial Institution/Court. Undertaking for the Black listing / debar is to be enclosed with bid documents on Rs. 100/- judicial stamp paper with duly notarized failing which price may not be opened.

5.    	TYPE TEST:

(a)	It is mandatory for the firms to submit detailed Test report issued by CPRI/ERDA/ERTL/NTH i.e. International Laboratory Accreditation Cooperation (in case of foreign laboratory) of similar rating and design of tendered material/equipment for basic feature check, as per IS 15959: 2011 with Tender offer in case of failure of its submission, tender offer shall not be considered for evaluation.

(b)	Such type test certificates should not be older than 5 years as on the date of bid opening. For this purpose date of conducting type test will be considered.

6.	The bidder shall furnish details of meters with specification, supplied by them in Govt./Power sector utilities,  during the previous five years along with copy of orders received purchaser of similar quantity & rate of failure of supplied meters. An affidavit in this regard shall have to be furnished with the offer.

7.   	DATE OF CONSIDERATION:

The above cited experience and manufactured quantities shall be counted as on the date of opening of the tender. All statements and claims should be duly supported by authenticated copies of documents without which the tender is liable to be rejected summarily.

8.       SAMPLES TO BE SUPPLIED BY THE SUPPLIER

03 (three) nos. sample meters duly signed by permanent marker by firm representative are to be submitted along with type test report with the offer, which shall be tested at any test lab of UPPCL by the Discom at supplier cost.

8.1 	Testing of samples:

Testing of samples submitted by the firms shall be tested on the cost of suppliers at its place decided by the Discom as per technical specifications given in NIT, in presence of firm’s representatives. Date of testing will be informed to all bidders. After receiving test result as per technical specification given in NIT any other observations made by test lab of UPPCL further decision will be taken for opening of price part.

AND

9.0	Final Testing of meters: (In compliance to Director (Distribution), UPPCL letter no. 2450&jsLIkks@lkSHkkX;@ehVj fof'kf"V fnukad 20-07-2021) (Enclosed)

9.1

- Testing of meters will be done at CPRI Lab only.

- On offer of meter inspection by the meter manufacturing firm an inspection team of  minimum two officers conversant with meter from the Discom(not below the rank of Executive Engineer) will be formed which will select the meter samples randomly from the meters offered for inspection as per clause no H2.1 of Annexure H of IS 13779:19999.

- Inspection team will seal the sample meter in their presence and will clearly note down the meter & seal number in their sealing certificate. Inspection team will get the sealed meter samples enclosed in packing in such a way that there is no way of tempering the samples in their presence. Inspection team will mention on their sealing certificate serial number of each seal with their specimen signature and this will be mentioned in inspection report.

- Meter manufacturer will be fully responsible for payment of all expenditure involved in delivery of the sealed and packed meter samples to CPRI lab by Inspection team, bringing back and all kind of testing charges.

- CPRI lab will test all the Acceptance Test on sample meters as per IS 13779:19999(With all latest amendments) in which following process is mentioned-

H-1 LOT

H- 1.1 In any consignment, all the meters of the same type and rating manufactured by the same factory during the same period shall be grouped together to constitute a lot.

H- 1.2 Sample shall be tested from each lot for ascertaining the conformity of the meters to the requirements of specified acceptance test.

H-2 SCALE OF SAMPLING

H- 2.1 The number of meters to be selected from the lot depends upon the size of the lot and shall be in accordance with Table 26.

| Table 26 Sampling Plan |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Lot Size | N 1 1 | N 2 2 | (N1+N2) | C1 | C2 |
| 1 | 2 | 3 | 4 | 5 | 6 |
| Up to 300 | 8 | - | 8 | 0 | - |
| 301 to 500 | 13 | 13 | 26 | 0 | 2 |
| 501 to 1000 | 20 | 20 | 40 | 0 | 3 |
| 1001 and above | 32 | 32 | 64 | 1 | 4 |
| 1) Size of the first sample. |  |  |  |  |  |
| 2) Size of the second sample. |  |  |  |  |  |

H-2.2 The meters shall be taken at random from the lot. The procedure given in IS 4905 may be adapted.

H- 3 NUMBER OF TESTS AND CRITERIA FOR ACCEPTANCE

H- 3.1 Test of No-Load Condition and Starting Condition

A sample of N1 meters selected according to col 2 of Table 26 shall be tested for the above tests. Any meter failing in any one of these tests shall be considered defective. If the number of defectives found in the sample is less than or equal to C1 the lot shall be considered to be conforming to these tests. If the number of defectives is greater than or equal to C2, the lot shall be considered as not conforming to these tests. If the number of defectives is between C1 and C2, a further sample of N2 meters shall be taken according to col 3 of Table 26 and subjected to these tests. If the number of defectives in two samples combined is less than C2, the lot shall be considered as conforming to these tests, otherwise rejected.

H1- 3.2 (i) Tests of insulation resistance, (ii) AC voltage tests, (iii) Test of power consumption, (iv) test of meter constant/registration. (v) limits of error and interpretation of test results and adjustment (if required).

From the sample of meters which have been drawn according to H-3.1 and those that have passed all tests of H-3.1. A sample of 8 meters shall be tested, all of which shall pass for conformity to these tests. If any of the meters fails in any of these tests, the whole lot shall be declared not conforming to the requirements of these tests.

H- 3.3 Tests for Repeatability of Error

Above tests shall be carried out on 3 samples selected from above 8 meters under H-3.2 and shall be tested for repeatability of error tests separately. If any one of the meters fails the whole lot shall be declared not conforming to the requirements of these tests.

H- 3.4 The lot shall be considered as conforming to this specification, if provisions of H-3.1, H-3.2 and H-3.3  are satisfied.

9.2  	All tests other than 9.1 which are not performed by the CPRI lab will be performed by Inspection team  of Discom as per standard technical specification for Energy meter issued by Power Corporation at the meter manufacturer works which are as below-

- Electronic Energy Meter.

- Display Parameter & Type of Display (Except those tests, which are covered in acceptance test at CPRI).

- General Requirement.

- Temper & Fraud Protection.

- Printed Circuit Board.

In addition to above, the inspection team shall also have to conduct any other tests prescribed by the Discom in the Tender Bid Specification.

9.3	CPRI has given written consent to test sample meters as per all Acceptance Test mentioned as per IS (With all latest amendments) within 10 working days. So, other than sampling of meters, packing by Inspection  team and testing of meters by CPRI as per Acceptance Test, if sample meters are found as per standard(by Inspection team) in other test(as mentioned in technical specifications) then the meter manufacturing firm after 15 days from the date of delivery of sample meters to CPRI Test lab on its expenditure may deliver the meter to different stores under Discom as per the directions issued by the “Engineer of Contract” but these meters will not be used neither for installation on consumer premises nor any payment will be done against this supplied lot of meter till the CPRI test report received. In case of getting CPRI Test lab report not as per standards then meter supplying firm has to take back all the meters of that lot from different stores on its expenditure.

9.4 	If during inspection by Inspection Team or Acceptance Test by CPRI meters are not found conforming to technical specification following penalty will be imposed on the meter-manufacturing firm-

| Case | Failure | Penal Action |  |  |
| --- | --- | --- | --- | --- |
|  |  | Replacement | Financial Penalty | Debarment from business/Blacklisting |
| Failure-1 | 1st time failure in fresh lot | 100% | NIL | NIL |
| Failure-2 | 2nd time failure in subsequent lot or replaced previous lots of same PO | 100% | 10% of the ex-works (including F&I) value of the lot plus GST. | NIL |
| Failure-3 | 3rd time failure in subsequent lot or replaced previous lots of the same PO | 100% | NIL | Debarment/blacklisting from business in All DISCOMs for 1 year (+) encashment of performance bank guarantee. |

9.5  	Discom will ensure that sample meters sent for testing to CPRI, after successful testing, must be received at a single store as far as possible.

9.6 	Meters offered for inspection must be tested for meter reading instrument / BCS by the Discom Inspection team.

9.7 	Purchaser at his discretion may consider awarding trial order of small quantity to those bidders who have proven design and meet the requirements. Such suppliers shall continue to be eligible for trial orders under this clause until their equipment has given three years of trouble free operational service.

9.8	For any type of typographical error in complete bid documents can be clarified separately from Discom.

All statements and claims regarding turnover, operational and manufacturing experience should be duly supported by authenticated copies of documents without which the tender is liable to be rejected summarily. PVVNL may call the tenderer to produce original purchase order/dispatch instruction or any other document for verification of submitted document during the evaluation of their bid.

*************************