Tender specification no. PVVNL-MT/COM/31(s)/21-22

TECHNICAL SPECIFICATION FOR 11 KV PT

1.0	GENERAL:

  - This specification covers the design, manufacture testing and supply of 11 KV PT.

  - The PT shall comply with the requirements of the relevant I.S. specifications.

  - List of raw material to be along with the name of suppliers should be submitted with the 	tender.

2.0	ELECTRICAL COMPONENTS:

The supplier shall be original manufacturer of the epoxy resin cast PT or accredited representative of such manufacturer. The bidder must have facility to cast epoxy resin by hot casting process under vacuum for PTs at his own works. These PTs should have been type tested  as mentioned elsewhere in the tender specification as per relevant ISS (latest revision) in a Govt. accredited National Test House such as CPRI, Bangalore / Bhopal etc during the last five years from the date of Tender opening.

3.0	THREE PHASE POTENTIAL TRANSFORMERS:

These will be dry type Epoxy resin cast, air-cooled and as per IS: 3156/1992 or latest amendment thereof. The primary and secondary winding of 11 KV PT should be wound on insulating craft paper. Entire PT assembly i.e. Core and Coil should be encapsulated under vacuum impregnation in Epoxy Resin. The PTs. shall have a ratio of 11 KV / 110 V and with a rated burden of 25 VA and of accuracy class 0.5. The material of primary and secondary winding should be copper. The cross sectional area of primary should be 0.04 sq. mm(minimum), and the secondary cross sectional area should be 1.6 sq. mm (Minimum). These will be connected in star-star for phase-to-phase voltage ratio of 11 KV/110 V. There will be no HT fuses in the primary side and secondary side of the potential Transformers. Rated voltage factor of PT should be as per ISS. Potential transformer should be type tested and routine tested as per IS: 3156:1992 or latest version thereof.

#### 3.1       The final layer of primary winding of potential transformer should be re-reinforced with extra insulation and then a equipotential /electro static shielding is to be provided.

#### Material

(i)	Core	High-grade non-ageing electrical low loss core of superior CRGO silicon sheet steel.

(ii)	Conductor			Super enameled copper wire

(iii)	Insulation			Resin cast.

(iv)	Base 				MS Hot dip galvanized.

- Primary termination 		Tinned Copper strips with sleeves 50x6 mm size as      				per relevant ISS, with clear polarity making P1&P2.

The strips should be suitably so bended as to 	facilitate smooth jointing with 11KV incoming and 	outgoing cable lugs.

(vi)	Secondary Termination	Firm and effective Termination with clearly polarity 				marking s1 &  s2

4.0	MAKE OF THE COMPONENT:

List of raw material to be used along with names of the suppliers should be submitted with Part-I & II of the tender. Make of various components as detailed above and as   being 	given below.

4.1	HARDWARE:

Hot-Dip Galvanized of any standard make.

4.2	PAINT:

Epoxy – Paint of standard make.

  - EPOXY RESIN :–

Dr. Beck, Huntsman, Atul.

5.0	INSPECTION AND TESTING:

All PTs shall be inspected and tested at manufacturer works to verify that these are being supplied in accordance with relevant standards. Technical Specification, Guaranteed Technical Particulars and acceptance and routine tests.

Inspection of material offered for inspection shall be carried out by the representatives of Superintending Engineer (Quality Cell), PVVNL, Meerut.

While offering for inspection /testing confirmation to the effect that the cubicle have successfully withstood the routing tests (along with test results)  is required to be submitted for each lot offered for inspection Superintending Engineer (Quality Cell), PVVNL, Meerut.

All testing equipment used in inspection and testing should be properly calibrated and sealed once a year. Calibration certificate when demanded by the inspecting officer shall be provided / produced for verification purpose. In case of any dispute regarding calibration, instruments shall be sealed and singed by the representative of the supplier and purchaser and will be sent to test house / Govt. Lab / Govt. institution of repute, for calibration at the cost of supplier. The result of such testing shall be binding on the supplier.

Purchaser reserves the right to get the PT's  inspected / type tested before dispatch by any independent inspection agency at the cost of purchaser in case the equipment with stand the type test, otherwise the supplier has to bear such cost in addition to any other action deemed appropriate by the purchaser.

One sample of PT of any ratio randomly selected from each offered lot, shall be opened for verifying the diameter & cross sectional area of primary coil conductors including verification of GTP

Testing Facility: - The manufacturer must have testing facilities at their works as per clause No. 1.2.3 of "Instruction to Tenderer" to carry out all the routine & acceptance test (including partial discharge test) as mentioned below. List of Testing equipment with photo copy of calibration certificates should be enclosed with Part- I of the tender.

5.1	Type test:

All the type tests as listed below shall be carried out for the equipment strictly as described as per the relevant ISS (or latest amendment thereafter).

Potential Transformers: (As per IS: 3159 / 1992 or its latest amendment. Type test on PT shall be done on any one unit

- Determination of error according to the requirements of accuracy class.

- Temperature rise test.

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

- Impulse Voltage Test.

5.2	Routine Tests: -

5.2.1	Potential Transformers:

a)	Verification of terminal markings and polarity

b)	Power frequency dry withstand test on primary windings.

c)	Power frequency dry withstand test on secondary windings.

d)	Determination of error according to the requirements of appropriate accuracy class.

e)	Partial discharge test in accordance with IS: 11322 / 1985

5.3	Acceptance Test:

5.3.1	Potential Transformers

a)	Verification of terminal markings and polarity

b)	High Voltage power dry withstand test on primary windings.

c)	High voltage power dry withstand test on secondary windings.

d)	Determination of error according to the requirements of appropriate accuracy class.

e)	Temperature rise test on any one selected sample.

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

f)	Partial discharge test

6.0	In case of any discrepancy between specification and relevant standard, provision contained in this specification shall prevail.