Implementation guidelines for deployment of multipoint dual source metering

Table of Contents

Background	3

Selection/ Empanelment criteria and scope of Solution Provider	14

Functional Requirements	30

# Background

As per the provisions of Electricity Act 2003 and UP supply code 2005 amended time to time, DISCOMS under PVVNL has been sanctioning single point electricity to various group housings, Multistory buildings and commercial shopping centers falling under DISCOMS under the PVVNL jurisdiction. These connections are either in the name of Builder or RWA who are deemed franchisee of the DISCOM. This system is being followed since more than a decade and predominantly private builder built housing complexes use single point connection at the society level and provide prepaid metering for individual units.

Current infrastructure deployment based on Single Point Connections

As of now, the entire in-premises electrical infrastructure is installed, operated and managed by builders as this single infrastructure gets utilized for both types of supplies – Utility power and DG using Dual Source Meters.

The description of such a system, as inspected and found at various group housing societies is as under:

- ONAN or dry type transformer of high capacity (more than 400 KVA) to save space for electrical installation

- 33KV to LT direct conversion to save space for electrical installation

- Common LT Panel for Utility power & DG.

- Single Cable from LT Panel to Meter Board.

- Single Meter Panel with Dual Source Meter.

- Change-over at LT Panel for Utility power & DG Supply.

- Floor wise meter board on various floors of multi-story high-rise apartments.

- Usage of high capacity transformers and switchgears normally not used by Utility.

Consumer Grievances:

In recent past, several complaints were received from housing societies individual consumers that the respective maintenance agencies / RWA are charging exorbitantly and arbitrarily in violation of tariff order issued by the Hon’ble UPERC, leading to loss on the part of consumers. Considering the issues and concerns raised by consumers and to protect their interest, it has been decided to provide multi point connections, i.e. each flat need to have its independent connection from the utility.

The following is a compilation of grievances that came up from various consumers who are residents of such group housing societies where there is single point distribution:

- Builders are charging fixed charges as per the area sq. ft. though their contracted load is quite less, thereby generating profit.

- Builders are charging higher tariff than the tariff order.

- Builders are charging hefty amount to the tune of 25,000/- per KW for load enhancement.

- Builders are fleecing consumers by charging between Rupees 25,000/- to 50,000/- for prepaid electricity system.

- Builders are providing prepaid electricity by taking advance from customers and paying the electricity dues on postpaid basis. In various cases builders have collected electricity charges in advance but have not paid electricity bills. This led to disconnection of electricity supply to the Multi-storied building. Since, consumers have already paid the money for electricity consumed in advance to the builder or RWA, disconnection by utility leads to litigation by consumer. Though in these cases builders/ RWAs are at fault, still end consumer suffers due to default by builders/ RWAs. With no option left consumers had to take recourse through legal means leading to litgations. In such cases, neither utility is at fault nor end consumers of electricity, but utility suffers losses due to litigations pending in courts.

- Majority of the builders are not providing monthly electricity bill detailing utility and DG units consumed by the customers which is a violation of CEA metering guideline/UP Supply Code Guideline.

- In various societies, builders have not installed suitable power management system while deploying prepaid electricity infrastructure for monitoring of Utility power failure (outage) time/DG running time with date & time stamp for verification with supplying substation under PVVNL for any discrepancy.

- Further, builders disconnect Utility power Supply for collection of other charges like maintenance charges, etc. which contradicts the guidelines laid by the Hon’ble UPERC. The guidelines suggest that electricity from Utility power should not be disconnected if consumer has paid for Utility power Charges.

Feasibility study undertaken by core committee:

Constraints & Solution for Conversion

| Issues | Findings | Deliberation and recommendation |
| --- | --- | --- |
| Metering of consumers | Dual register meters are being used in all multistory buildings having single point connection | Dual meters to be used to avoid any additional infrastructure cost. Also, creation of dual infra will need additional space which is not feasible. |
| Same service cable is being used to supply Utility power/ DG power to consumers. To record Utility power and generator power in different registers of the meter for billing, which technology to be adopted. | Following types of technology is being used to differentiate Utility power and generator power: - DG running information broadcast through Radio frequency-based mesh network – new buildings - Signal injector- older buildings - Connecting every meter with wire for DG run signaling – old buildings | It was found that all these meters have two registers in which Utility power consumption is recorded in first register and DG power is recorded in second register. To discriminate source of power and to register them in different registers, meters are getting signal to switch registers. It was concluded that energy meter should record Utility power in default mode. Only in case of generator power, meters should be given command to switch register. Radio frequency-based mesh network is recommended as there is least chance of physical tamper. These are being used satisfactorily in new buildings. |
| How to bill customers through one meter based on dual supply | All billing and calculations are being managed at software level and not meter level |  |
| Other findings | - All the metering establishments are found without seals - Different makes of meters are being used which generally and presently not procured by DISCOMs of UP. - The space in the metering room of each floor and meter boxes are too small. The present size of meters with transparent box cannot be installed. - Electrical infrastructure, transformer and switchgears are of different specifications than the DISCOMs specifications and cannot be maintained by DISCOMs due to unavailability of these items with DISCOM. - Generally, all such group housings have engaged services of third parties for metering & billing and maintenance & management of electrical infrastructure. |  |

| How to credit the amount for generator charges to RWA? How to achieve Dual accounting through Dual meter? How PVVNL will come to know monthly DG amount to be credited to RWA? | Since there are two types of supply source to consumers and PVVNL billing system has no provision for generator billing through dual meter, it is required that PVVNL should implement prepaid electricity system for UTILITY POWER and generator billing system should remain prerogative of RWAs. Since, meters have dual register and are recording Utility power consumption in one register and generator consumption in another register, there should be dual accounting mechanism in the back-end also in which based on utility power consumption by consumer, prepaid functionality shall be implemented by DISCOM and based on generator consumption data, RWAs shall manage their accounting. It recommended that DG metering data shall be provided to RWAs through web / cloud based access controlled services. As per present practice, it is observed that on the back-end system utility power data and generator data are being recorded separately. Similar mechanism may be adopted. |
| --- | --- |
| In case if Utility power supply is available and by mischief DG mode is made ON in the meter; Utility power units will be registered in generator register causing loss to DISCOM as well as the consumer will raise concern of high charging and the perpetrator will get money. How do we achieve fool proof mechanism for register switching in dual meter? | In the dual metering system grid & DG supply can be monitored at back-end, malfunction can be detected through the various logic like sending notification to concerned officials and affected consumers etc. of the exceptional situation when Utility power is available at building and DG power is being registered in the consumer meter. Since both the data shall be available at the back-end system, such software logics and related response mechanism should be created. |
| DG rate is constantly varying due to diesel price variation. How to provide right to RWA to change generator unit cost? | By providing DG data on separate cloud, rights related to tariff, billing, load control and charging mechanism will be in the control of RWA. |
| If someone bypasses the meter, how will the DISCOM come to know? If in case of not being able to identify the issue, billing the same to RWA will lead to dispute. | Agency which will operate and maintain the system will be responsible for the near real time energy audit and reporting the exception to DISCOM and it’s field officials on immediate basis. |
| There will be credit balance in almost all the connected prepaid meters, hence, DISCOM will be having money with respect to the whole complex in its account. As per norms in prepaid metering, DISCOM is not taking meter reading. How will we arrive at common area loss and how the loss will be billed to RWA? | Standalone prepaid meter shall not work in these buildings. Only AMR based meter with prepayment functionality implemented through back-end can handle the complexity of dual metering in such buildings. |
| Where should meter data reside? | Meter data should first land at UPPCL data centre. The head end system (HES) at utility will receive meter data and the same can be bifurcated further into two databases. One database shall keep utility power data and another data base shall keep generator data. |
| How to bifurcate ownership of meter reading? Can DG meter reading be forwarded to another server outside UPPCL DC? | Generator database can be synced with external server outside of UPPCL data centre. This external server shall be used by RWAs for billing and other charging and control mechanism. |
| UTILITY POWER and DG balance be kept into two separate registers so that even in case of zero balance in DG account, Utility power supply may continue? | There will be dual accounting system in which Utility power and generator accounts shall be maintained in two separate servers. Accordingly, there will be separate control over Utility power and Generator supply. Since, DG account is having zero balance, in case of power source being DG, meter shall disconnect the supply. |
| How to do energy audit? | LT CT Dual meter shall be required to be provided on all common area points. These meters shall also communicate with the back-end system. Since, all the consumer dual meters data is available at the back-end along with common area meter data, the energy audit shall be done after every 15 minutes. This will also ensure that no pilferage is happening. |
| Since DISCOM staff is not trained to handle dual metering issues, its management and billing for generator charges etc. how to implement and run such systems keeping in mind interest of DISCOM as well as RWA. - As of now, residential buildings are having single point connection, DISCOMs were not concerned regarding pilferage, energy loss inside these buildings. - Electrical infrastructure created at these buildings are of different specifications than the practiced specifications at DISCOMs of UP. Hence though DISCOMs shall provide direct connection to end users, maintenance of electrical infrastructure through which Utility power supply is provided to consumers cannot be taken up by DISCOMs. - DISCOMs of UP have never procured dual meters and neither have provision for billing based on dual meter in its billing system. - Metering at these buildings have grown in ad-hoc fashion. In some cases metering system provides good level of transparency by enabling consumers to track, monitor their electricity consumption in real time through mobile and web based applications, in some cases metering system is being misused to fleece customer by overcharging and no | - Engagement of implementation, operation and maintenance agency for buildings. - Fool proof solution including web/ mobile app for greater transparency to avoid disputes with RWAs and consumers. |

Brief Outline to implement Multi-Point solution on single point electrical infrastructure

The overall solution to implement Multi-Point Electrical Connections comprises of the following major steps:

- Empanelment/Selection of Solution Provider including facility management services also referred to as AMI Implementing Agency (AIA) by DISCOM with five years O&M service contract.

- Empanelment/Selection of Dual Source Dual Register meter manufacturers to supply these special purpose meters.

- Procurement and Installation of Dual Register Three phase meters for every metering point / unit to record the Utility and DG consumption precisely. The meters need to be preferrebly as per IS: 16444 or IS 13779 with IS 15959 DLMS support along with separate disconnection mechanism for Utility or DG supply. Also, LT CT dual meters as per shall be needed to be installed for installation on common area consumption points for common area energy billing/ energy audit.

- Integrated / Over The Top (OTT) arrangement (complying with relevant BIS standards if applicable) that work as nodes on meters and provide information like electric demand and energy consumption of consumers and other electrical assets deployed as part of electric supply infrastructure

- RF/GPRS/ 3G/ 4G/nbIoT/other secure communication network on (complying with applicable standards).

- Deployment of the communication infrastructure should be such that meter parameters of all the connected energy meters should reach to the back-end in near real time so that any anamoly in the system is detected instantly, near real time energy audit is done to avoid any revenue loss to DISCOM.

- Backend platform that can handle the data from both the sources of supply (Utility and DG) and process the data appropriately. The backend system should be able to bifurcate the data and pass on the DISCOM Energy consumption data to the respective DISCOM for billing / accounting and the DG Energy consumption data to the RWA/Builder/Service Provider’s cloud for appropriate accounting and billing on their part. The PVVNL Billing part needs to work in Pre-paid mode. For the DG part, it will be the choice of RWA/Builder/Service Provider whether they want to operate on Pre-paid or on post paid basis.

- AMR/AMI based solution with prepayment functionality implemented through back-end can handle the complexity of dual metering in such buildings.

To achieve the aforesaid objective, the broader guidelines shall be the model document issued by Central Electricity Authority in August 2016 with title Functional Requirements of Advance Metering Infrastructure (AMI). However, as AMI solution guidelines issued by CEA is mainly based on the requirements of Utility and Utility supplied power, to accommodate complexities of Dual metering on the same electrical distribution infrastructure in these multistorey buildings, the solution to be adopted should be balanced enough to meet the statutory requirements laid down by CEA and other statutory Authorities as well as to handle the complexity of DG power, transparency in handling consumer issues that may crop up.

Since, such dual meters get command to change its registry from one source to another source, a fool proof mechanism of source change along with alerts/ notifications must be in place to avoid revenue loss to utility as well as end consumers.

System Features:

Based on the site visits, observation of some existing single point solutions and deliberations done by the committee, the following are the features that the system should be able to cater to:

- In all such buildings where single point is being converted into multi point connection, dual register meters needs to be used.

- Metering to be done at all the points required for energy audit/billing including HT/LT CT Meters if required. Bidder has to read the data of such meters through Modem/gateway and use it for energy audit & billing

- Dual metering system for UTILITY POWER and DG power needs to be fool proof. Robustness of this shall avoid any confusion with RWA and DISCOM in future as discrepancy in this data shall lead to litigation.

- Utility power register should be default mode for registration of power supplied to customers. Generator mode should be triggered when generator supply is being fed into electrical distribution network.

- The meters used should have in-built disconnection facility as well as communication facility with latest DLMS protocol.

- Prepaid metering functionality should be back-end controlled so that mode of metering and billing operation may be adopted as per the choice of either utility or of RWA.

- There must be two sets of prepaid recharge coupon- one for UTILITY POWER supply and another for DG supply.

- UTILITY POWER recharge coupon needs to be integrated with PVVNL revenue management system. All integration has to happen with automated processes.

- DG meter data to be forwarded to another server/cloud with access control through unique login for different RWAs and DG billing to be done by RWA.

- DG tariff is to be decided by RWA, hence DG revenue management system to reside outside of PVVNL data centre/ server. PVVNL to provide only DG consumption data to outside server.

- DG revenue management, collection on postpaid / prepaid shall be choice of RWA/ Builders. Any amount pertaining to DG meter data shall accrue to RWA account. PVVNL shall not have any intervention in this system.

- Energy accounting shall be done by PVVNL for UTILITY POWER supply only. Energy accounting for DG shall be done by respective RWAs.

- While as per meter data received, PVVNL shall process UTILITY POWER reading as per its established practices like billing, disconnection, load control, etc., and for DG data RWA shall be free to implement their own mechanism.

- Notification and alert for pre-defined exceptions like higher energy loss than defined limit, meter registering energy while Utility power is available, etc. and Real time energy audit should be available with 15 minutes granularity on back-end system.

- For transparency and to avoid any issues related to Utility power / generator power consumption issues and charges being deducted for common area power, a real time mobile based application as prevalent in these buildings should be adopted.

- Floor wise metering may also be allowed to counter space restraint and to mitigate any pilferage. (In case of such availability).

- Energy accounting and Common area electrical charges mechanism to be deployed based on AMI/AMR.

- Due to space constraints in the meter board/ small size of meter compartment, compact meters. PVVNL may opt for multiple makes of meters for consumers of group housing complex.

- Essential clauses and capabilities of the Dual metering infrastructure agency must include to provide centralized monitoring, NOC, generate alerts and reports as desired by DISCOMs.

- DISCOMs may appoint a nodal officer based at HQ to monitor the implementation and compliance. Apart from this, contractors shall be required to be dedicatedly deployed based on the size of society and manning standards.

Recommended Approach for implementation of Multipoint

- AMI/AMR solution providers and/or meter manfacturers may be empaneled to  deploy, manage and maintain AMI/AMR network at building level.

- Empanelment of only those solution providers having technical capability and experience to provide Dual HES for dual metering including deployment of Server as well as can maintain uptime of server as per utility defined SLA. The empaneled solution provider to be capable of providing UTILITY POWER data to PVVNL billing system in desired format like MIOS and should be capable to integrate with PVVNL revenue system.

- PVVNL to sign tripartite agreement with telecom service provider for M2M APN SIMs through which AMI/AMR data in a secured manner land at HES at backend.

- Other costs such as AMC of electrical infra/ management cost of internal system shall be responsibility of Developer/ RWA.

Technical aspects

Proposed Architecture

Brief introduction of IT Infrastructure at PVVNL:

Existing IT system of PVVNL is based on unified access framework. The applications systems are built upon WS* specifications using open industry standards of Web services using XML, SOAP, WSDL and UDDI. Hence PVVNL intends to use existing integration middleware that is based on Service Oriented Architecture (SOA) and uses publish / subscribe mechanism, to move data between existing and proposed dual metering AMI/AMR system, without duplicity of resources and with minimum overheads. Solution Providers are expected to have clear understanding in this regard and willingness to adopt methodology that helps to build efficient and integrated system to achieve the intended objectives.

- Customer Care & Billing (CCB):

This refers to Billing System being used in PVVNL. The various modules available in CCB are New Connection, Metering, Billing, Collection, Disconnection, and Customer Care Center. New Connection deals with the procedure when a consumer applies for a new connection to power utility. Metering includes installation of new meters, maintaining meter reads, managing meter information, maintaining stock for meters. Billing includes manual and automated bill generation, rates on the basis of which the bills are generated, bill message, bill printing, downloading & uploading bills through Spot Billing Machine (SBM)/Mobile App Billing, manual adjustments, and so on.

Collection includes accepting bill payments through different modes, partial payment approval & acceptance, and so on. Disconnection aims to cover the process of utility initiated and consumer requested disconnection. Customer Care Center deals with the process that describes the management of consumer service by processing and resolving consumer requests/queries/complaints in minimum possible time by taking up it at appropriate place and level.

The various features of Collection module are listed below:

- Different Mode of Payments at Cashiering Station: Consumer can pay their debts in Cash, Cheque, DD, Credit / Debit Cards.

- Other payment options: Consumer can also pay their debts through Internet using Net Banking, ECS

- Acknowledgement of Every Payment: Consumer will get SMS/Email acknowledging the payment made

- Triggers for payment reminder: Consumer will get reminder SMS/Email alert before due date, to avoid late payment charges and disconnection

Meter Data Acquisition System (MDAS) and Energy Accounting (EA):

This refers to Meter Data Acquisition System and Energy Audit. MDAS aims at automating meter data collection from system meters and HT / selective consumer meters on scheduled or request basis, meter data validation, generation of alarm & notification based on condition of system parameters. The system provides load survey parameters, energy parameters, and meter events of AMI/AMR metering points for network analysis, billing & energy audit purpose.

EA deals with energy audit of power distribution utility which analyzes data irrespective of meter make. The system enables to calculate HT loss, DT loss, Aggregated Technical & Commercial (AT&C) loss for selected area/network. The system also computes various losses using network data & configuration details from GIS, meter data from MDAS, billed energy, billed amount and collection amount from MBC.

# Selection/ Empanelment criteria and scope of Solution Provider

This section provides functional requirement of the Multi-Point Dual  Metering AMI/AMR system intended to be installed along with the guidelines and methodology that will facilitate successful installation, integration, operation and maintenance of a range of Dual Metering AMI/AMR functionalities described in subsequent sections and technical specifications.

a) Multi Point Dual Metering AMI/AMR solution is intended to create an intelligent communication network between the Dual register dual source meters installed at various location i.e. towers, buildings consumer premises etc. and the utility business systems. The Dual Metering AMI/AMR network shall facilitate collection of metering information automatically and Network Operation Centre and passing on the alerts / reports obtained from the meters to the designated offices and officers of utility as described in the technical specification.

b) Desired solution shall not only work for collection of metering data, but should be designed to make possible availability of real-time distribution system information on existing Servers/ Operator work stations (PCs) installed in Network Operation Centre. The Dual Metering Multi Point AMI/AMR system should be able to provide following main functionalities: -

    - Automatic Meter Reading of the Consumers / meters for Multi Story complexes as identified by PVVNL for both sources – Utility power and DG

    - Bifurcation of metering data received at Dual Metering AMI/AMR HES and posting of Utility power reading in separate database and DG reading in separate database.

    - Real time supply source information without any time-lag, real time display of supply status on the dashboard prepared for individual Group housing sites, monitoring with alerts and alarm to designated numbers of any deviation/ discrepancy compared against Utility power power availability vis-a-vis change of source of power at building and also at consumer level.

    - Demand Side Management / Load Management for Utility power.

    - Energy Accounting and auditing.

    - Administrator and Maintenance Portal

    - Generation of automatic alert / alarm and notification of the same through SMS and Email to designated officers of PVVNL.

    - Provide system outage / downtime data.

    - Provide cumulative daily peak load in the building vs. recording at single point meter with time stamp.

    - North Bound Interface for integration with existing billing system of PVVNL.

    - Providing centrally administered prepaid electricity engine for Utility power with different tariff category on unified infrastructure.

    - Automatic remote disconnection through prepaid engine on exhaust of prepaid balance and automatic reconnection of consumer load when UPPCL billing system provides information of individual consumer recharge to prepaid electricity engine deployed by AIA.

c)  Solution provider (also referred to as AIA) will design appropriate architecture for providing end to end metering solution. AIA is free to decide upon the best solution out of all the available options. However, the entire responsibility of fully functional AMI system shall rest with one agency i.e. AIA in order to meet the performance levels as given in this document. The AIA may adopt Radio Frequency (RF) mesh in license free frequency band/ Power Line Carrier Communication / Long range radio or GPRS/3G/4G/nbIoT communication technology or RF based canopy system or a combination of these technologies as per the site requirement adopting best available technology in the proposed area of implementation.

d)  The main objective of implementing the bidirectional meter communication and remote data acquisition system is to acquire meter data automatically from different meters and for both sources (Utility power and DG), monitor important distribution parameters, provide meter data to billing system for accurate billing and reporting, generate and dispatch notification on any abnormal activity / parameter in the network and use the data for several other analytical applications.

e)  Implementation of AMI/AMR system implies the amalgamation of three major components i.e. Meters, Communication media and the Meter Data Management along with the required Dual- metering Head-end systems and other applications. The AMI solution as envisaged for PVVNL shall comprise of Dual Source Meters with OTT node interfacing with meter’s optical / CMRI/ NIC port and shall push the meter data and alerts automatically at definable interval.

f) 	The complete AMI solution should work on RF mesh technology or any other technology after the approval from PVVNL for communication of consumer meters data with data aggregators/concentrators. The meter data from aggregators will be transmitted through secured M2M APN based GPRS/3G/4G network terminating its aggregated traffic through MPLS links. The dual metering AMI system shall sync DG data to backend server with external server through private MPLS link not having internet access to provide DG data to developer/ RWA for their processing and operations.  Since the same meter shall be used for receiving and acting on commands for Load control or disconnection issued by developer/ RWA software system, only predefined and pre-approved formats will be allowed to pass through Dual Metering HES system. No commands other than pre-approved shall be accepted by Dual Metering HES system.

g) The proposed system is expected to provide continuous on-line monitoring and logging of essentially, though not limited to, the following parameters in respect of all consumers for Utility power and DG supply on near real time and/or scheduled basis: -

i.	Phase wise Voltage

ii.	Current on each phase

iii.	Power factor

iv.	Frequency

v.	kWh

vi.	kVAh

vii.	kW

viii.	kVA

ix.	Maximum Demand

x.	Outages

xi.	Reading in TOD registers.

xii.	Other available parameters.

- The System must also have the capability to implement and integrate with advance analytical applications. The System should be based on the following principles:

- Interoperability: Should be capable of integration with existing systems of PVVNL.

- Reliability: High up time

- Scalability: Should support at least 5 Lac consumer base to be migrated to new multi-point system.

- Flexibility: The system should be flexible and adaptable to new requirements from time to time.

- Modularity: PVVNL, as per requirement, should be able to implement any permutation and combination of the functionalities, as stated above and in future the system deployed should be upgradable to include any of the features mentioned in this document.

i) Through Single point meter the AMI system should be able to constantly monitor the following parameters to take proactive measures. The functional Requirements for the same are as below:

- Integration of existing HT Energy Meter installed at single point.

- PVVNL should be able to correlate events coming from different sources e.g. Outage event coming from a meter/ other equipment in the network and an outage event coming from the single point meter in the network to which the consumer is connected.

- The system should have the capability to generate alerts for different events. The system should also have the capability to assign the appropriate person for the alerts to be sent as identified by PVVNL for various types of alerts.  Example of the Alerts are

  - Voltage imbalance in the phases

  - Power factor falling below a certain level.

  - Current and Load imbalance beyond defined limits.

- Many developers are developing projects in phased manner and they take electricity connection for initial phase of the project to provide electricity to the occupiers of the complex. To stop unauthorized use of common power for construction purposes, System should be capable of sending out alerts in case the un-usual load pattern is observed. In case of such events, the alert should be sent to appropriate team as identified by PVVNL.

j)	The system should enable PVVNL to carry out Multi-Story Premises wise energy accounting, which will account for the total energy output from the utility side and the consumption of the same at the customer level and common area facilities, wherever applicable and identify losses that will be required for accounting settlements with Builder/RWA.

- With the injection and the consumption points covered, a near real time energy accounting should be achieved.

- With the help of energy accounting, T&D losses, commercial losses like Theft, tamper would be detected. The AMI system shall inform PVVNL all such societies registering losses beyond permissible limits as per directives of PVVNL.

- In case of deviation, beyond permissible limits, between the export of energy and consumption recorded by all consumer/ common area meters, alerts should be generated and the concerned PVVNL staff should be notified. It will also help in identifying faulty meters and events of meter bypass at all levels.

k)	AMI should be able to monitor power quality parameters as well as consumer connections like

- Power factor

- Power on/off

- Over Load and under Load

- Over and under Voltage.

- Over Current and under loading.

System should provide alerts to PVVNL on violation of threshold values as and when occurred/recorded. The system should be able to provide supply outage report at single point HT meter level also.

l) 	The system should enable PVVNL to implement following functionalities, under the load management initiative:

- Remote disconnection of customer service connection due to prepaid balance being insufficient or any other payment default or limiting the load of the customer to a certain limit to manage load within available supply during peak hours.

- Remotely reconnect or resume load to normal contracted load level following payment (disconnected due to payment default) or if demand supply gap narrows.

- To limit customer’s load, say for reasons like exceeding contracted load (and then increase in contracted load on regularization/enhancement request by customer is acknowledged and accounted for).

- System should issue notification to consumers violating the contracted load and to utility to take necessary action under regulatory frame work.

- Remotely disconnect / reconnect customer load on customer request.

Similar features or as desired by RWA/Builder should be available for managing, accounting of the DG Supply since supply source will be on their part.

The Installed devices should send acknowledgement of successfully completed and failed disconnects, load limiting and reconnects to the back-end system.

m) 	The consumer portal should give consumers access to view their own consumption. This will help them to take informed decision on optimizing energy consumption based on the tariff and source of supply (Utility power / DG) as per regulatory guidelines. Some of the functions that should be supported are as below:

- The customers should be able to view their live energy data on the portal for Utility power and DG supplies.

- The customers should be able to receive real-time messages on the portal / SMS/ Email in case of any alerts set by them.

- The customers should be able to view their historical data from the Web and app Interface.

- Utility should be able to notify the consumers on planned outages in their area.

- The Web portal and apps should have an access control, i.e. a username and password to access energy profile.

The consumer portal should be accessible from any web-based browser and app for smart devices.

Multi-Point AMI System components

- Dual Register Energy Meters for precisely recording Utility power and DG supplies.

- Communication infrastructure

- Head End System (HES)

- Meter Data Management System (MDMS)

- Web application with updated on-line data of consumers etc.

- Mobile app: Providing interface for consumer to log in through android/iOS based mobile app to see information related to his/her energy consumption.

I)	The selected/empanelled AMI Implementing Agency (AIA) / solution provider shall supply, install, test and commission all the equipment, material & software viz. Meters/ OTT module, data concentrator/ Aggregators, GPRS hardware, disconnection modules, the Meter Data Management System (MDM) application, the server along with any licensed software for hosting the same and other hardware and software applications which should form the base computer station (BCS). The MDM should be a web-based application which should be accessible from remote sub-divisions, circle and zonal offices. It should have integration features with the billing servers of PVVNL. The AIA shall be responsible to provide billing data of all the consumers under AMI in the format specified by PVVNL.

II)	The designated AIA may offer cloud based AMI solution on Miety approved cloud vendors. AIA shall undertake the operation and maintenance of the complete AMI system for complete contract period subsequent to its commissioning. The operation & maintenance charges will include replacement of defective equipment/ material supplied by the AIA, carrying out regular and periodic field activities required for ensuring proper health of the deployed infrastructure etc. The AIA shall undertake following activities:

1. Operate the entire Multi Point system including onsite support to maintain all AMI solution. For this, the AIA shall depute its personnel. PVVNL shall bear O&M charges related to licensee’s billing and the obligations for O&M charges on account of DG billing and data management management shall be borne by consumers and RWA.

2. The AIA shall also provide adequate manpower to maintain the system in the field for complete contract period from the date of successful installation and commissioning of the Multi Point system. The terms of such agreement shall be governed by tripartite agreement. Initially the contract period will be 5 year then it can further be extended on year to year basis on the same or lower rates on mutual acceptance. In case AIA is not interested to continue after complete contract period, he will give a six month advance notice to arrange a new AIA by Utility. The present AIA shall not be allowed to quit till a new AIA take over all the System. Equipment supplied by AIA shall be the property of PVVNL.

3. AIA shall be responsible for periodic testing, regulatory compliance certification on periodic basis and necessary upgrading of the back-end software and device firmware. AIA shall also be responsible for any modification in the back-end system, billing system as per the instruction of the DISCOM during contract period.

4. During the operation period, the AIA shall carry out various activities like generation of periodic MIS reports as required, updating of the database with respect to new consumers on the advice of PVVNL.

5. Timely responding and attending to various operational queries and troubleshooting of the problems and system malfunctioning.

6. The AIA will be required to provide adequate training to designated staff of PVVNL for proper handling of the system, before handing over of the complete system.

7. After handing over of the system, the AIA will continue to support PVVNL for supply of spares & trouble shooting for complete contract period. The terms and modalities for future support shall be discussed and decided at appropriate time.

III)	Scope regarding Communication Services

1. The AIA shall be responsible for providing the communication services between the Meters and the NOC/ Data Centre.  The Agency shall supply all the communication modules including GPRS/ 3G/ 4G SIM and modems, if required. The monthly charges to be paid to telecom service providers shall be in the scope of the AIA which shall be paid by him before due date to avoid disruption in service.

2. The installation and configuration of the routers or any other communication equipment(s) shall be the sole responsibility of the AIA.

3. All the equipment required to be installed at the consumer’s premises shall be installed inside the Meter Box. 4. All equipment that will be installed across the communication path (from dual meter to Data Centre), such as routers, modems and interface converters shall be installed by the supplier in a secure way and he shall be responsible for all cost associated with the installation.

Requirement of Mobile app

Mobile app shall be dedicated for UPPCL Consumers. Each user shall have their unique credential. First time login password shall be provided to user. The moment users sign in to mobile app, they shall be forced to change their password.

Back-end system shall have capability to map mobile numbers/ e-mail ID associated with user ID. Password reset request may be entertained through user linked mobile number or e-mail or combination of both.

Meter triggering process methodology and signal voltage range.

By default, meter shall measure energy in Grid mode. In case of DG running, DG signal shall be fed to the meter.

Hardware specifications required for solution/servers.

The hardware configuration shall be in the scope of the bidder to store & process data of 1 million  nodes. Bidder may opt for suitable configuration extendable to accommodate data of 1 million nodes. Bidder has to propose sizing of servers accordingly and has to upgrade as & when required to meet out the performance.

Process of DG data segregation from DCU/Gateway

The Dual HES system shall receive separated data for DG & Grid and store in different database.  Meter data shall be received by DCP (Dual HES) at DC. DG data shall be routed to RWA/Builder platform/cloud for billing & processing.

Billing engine features

Billing engine steps:

- Mapping of consumers in DB

- Mapping of consumers against DCU/ MCB ID.

- Mapping of tariff data.

- Real time meter data received from Gateway on HES.

- Validation and verification of received data

- Once Verified, Calculation of unit consumed as per the Tariff slab.

- Calculated amount deduction from user wallet.

- Wallet can be recharged through coupon / online payments options.

- After successful recharge amount credited to user wallet.

Alert types and Severity

- Gateway/ DCU/Meter disconnection -> Critical

- Low balance -> Moderate

- Grid power failure -> Critical

- Zero Load on meter -> Moderate

- Network Signal Strength -> Moderate

Methodology and Responsibility Matrix for implementing Multi Point AMI system

Involved Parties: DISCOM / PVVNL, RWA/Builder/Estate Management Agency; AIA

| SN | Functionality | Description | Responsibility |
| --- | --- | --- | --- |
| 1 | Survey of the building to physically identify the consumers. Consumer details including email Id & phone nos. to be recorded. | The AIA shall undertake survey of the allotted building. The role of AIA shall also be to prepare electrical distribution Single Line Diagram along with all the details like LT panel out goings, feeder pillars, rating of transformers, switchgears, size of cable, common area load and common area connected equipment, DG capacity and all relevant information. Consumer premises maybe visited by AIA in company of RWA/Builder staff only. | Builder / RWA –to provide all the technical details along with electrical distribution SLD etc. builder/ RWA to provide tower wise consumer list along with area statement. |
| 2 | Recording of current meter reading before installation of Dual Source Meter for proper reconciliation of billing as per defined process of meter change. | The AIA will provide the tower wise list of consumers with requisite details to RWA/Builder for reconciliation and accounting. | AIA- for providing the required details. RWA/Builder – For doing their part of reconciliation / billing etc. before the system migration from current single point to multi-point. |
| 3 | Installation of individual consumer dual source meters / OTT nodes | Installation of approved / empaneled dual meters with minimum interruption of power supply to consumers | PVVNL - to provide authority letter to AIA for accessing the building/ consumer premises during installation. AIA- to complete installation RWA/Builder – help facilitate the installation process under their supervision. |
| 4 | Reporting of the inaccessible house/ consumers | The AIA shall provide list of all the consumers whose premises are either locked or they are not allowing the AIA/ PVVNL staff for installation. | AIA - to provide the inaccessible consumers list. PVVNL - to take necessary action for gaining access to the reported premises RWA/Builder – help facilitate the installation process |
| 5 | Set up and commissioning of Servers/ routers/ switches and software | AIA shall install and commission the server and integrate the system with UPPCL back-end for billing and other functionalities. | UPPCL - for providing Air-conditioned space along with free power supply suitable for establishing the Dual Metering AMI servers and software. AIA - for all the supplies, installation, commissioning and operations for the specified period as per specs. |
| 6 | Remote capturing of meter data from consumer meters and other measurement points as per scope. | Should capture the meter data remotely from all the meters installed at electrical distribution infrastructure and Consumers for sending it directly to the head end system at DC/DR. | AIA |
| 7 | Provision of secured communication media | The system should work on RF mesh network data concentrator/ aggregator for data acquisition from consumer meters and DT meters. The Data Aggregator should work on secured GPRS/ 3G / 4G /MPLS or any other suitable secured communication technology between aggregator, consumers and HES at DC/DR. The aggregator shall have Dual Communication channel ( e.g. Dual SIM) one as active and another as redundancy between HES at DC/DR to meet uptime SLA. | AIA |
| 8 | Energy Accounting | Should provide energy accounting. The energy audit should be indicative of any potential thefts or pilferages. AIA shall create a web based portal for online energy audit with notifications/ alarms for defined exceptions like high T&D loss/ phase imbalance/ Low power factor etc. | AIA |
| 9 | Remote disconnection / reconnection separately for Utility power and DG supply. | Should provide remote disconnection / reconnection of consumer load for Utility power and DG Supply separately. The disconnection / reconnection mode should be both automatic (event driven) and manual (remote) mode as per the option of PVVNL. The system should support disconnection automatically say for load management and non-payment of dues by consumer. System should also support mass disconnection of DG supply e.g. black-out or grey out feature to comply with Environment Pollution (Prevention & Control) Authority for the National Capital Region (EPCA) instructions released time to time for NCR region. | DISCOM/PVVNL - for specific instruction regarding disconnections / reconnections for Utility power Supply RWA/Builder – for specific instructions regarding disconnections / reconnections for DG Supply. AIA for ensuring required operations |
| 10 | Decision support system | System should act as a decision-support system with distributed intelligence for: - - Peak load monitoring for augmentation of electrical network element to meet the increased demand / load growth - Power factor monitoring. - Voltage monitoring to identify low voltage areas. - Data capturing to identify imbalance between phases through single point meter, substation and 3 phase consumer meters to increase reliability/plan phase balancing / advise customer to balance load amongst phases. The system should identify poorly performing areas in the distribution network, based upon the technical parameters, such as area wise distribution losses, theft, outages, overloaded circuits/equipment, voltage imbalance, reliability indices, power quality. The system should provide flexibility to configure parameters for near real time monitoring and generating alerts / alarms basis the threshold values configured by PVVNL for parameters as Voltage, Current, Power Factor, Load and Frequency. Any similar monitoring parameters to be set separately for DG supply if required by the RWA/Builder. | AIA |
| 11 | Database upgrade actions | Release of new connections is a regular process in utilities. After initial creation of database for Society wise consumers, if any new connection is released for additional towers / consumers, the same will be required to be updated in the database. | PVVNL along with RWA/AIA shall prepare modus operandi for such connection request as well as provisioning data input along with details of concerned DT. AIA will physically verify the connection details at site in supervision of PVVNL staff and update the database. |
| 12 | Accurate and Reliable Detection of Power Outages and Restorations. | System should enable quick, ‘event-driven’ detection of utility power outages and immediately trigger the DG registry in the dual meter to start recording the backup power so as to have error free accounting of energy. The reverse phenomena should also be detected and acted upon with equal accuracy and reliability so that at no point in time, the source of supply should get recorded incorrectly. | AIA |
| 13 | Monitoring of consumer performances | System should enable monitoring of consumer performance, e.g. insufficient prepaid balance, contract demand violation, peak load violation, average power factor etc. The system should also have provisions to cover usage patterns to solve high consumption complaints, facilitate calculation of assessed readings for defective meter cases and detect low consumption cases. System should provide detection of faulty meters. System should enable, through consumer portal, access of performance parameters and meter consumption data to the consumer for participation in energy saving initiatives. | AIA PVVNL: to do follow-up actions based on the performance reports related to Utility power Supply. RWA/Builder: to do follow-up actions based on the performance reports related to DG Supply. |
| 14 | Enabling dispatch of event notifications | System should be capable of dispatching of event notifications to targeted recipients in the form of SMS/ emails for faster field response and decision-making. | AIA will be responsible for interfacing their system with PVVNL SMS gateway and the AMI system should issue alerts to the designated DISCOM and PVVNL staffs as per levels of the alerts defined by PVVNL. Any further management of SMS alerts from their server shall be the responsibility of PVVNL. The AIA may use its own SMS gateway for sending out SMS alerts on behalf of RWA/Builder if desired by the later. |
| 15 | Localized Intelligence | The OTT devices/ meters installed at distribution points should have the capability to perform load management functions, even in absence of connectivity to the HES, such as load management, parameter violation etc. except HES interpreted parameters and functions. | AIA |
| 16 | Generation of Reports | All the MIS reports / event / Energy accounting reports etc shall be made available at the server level of DC/DR/NOC which shall be accessible to designated officers of PVVNL through internet as identified by them. | AIA to ensure the functionality and provide user name and Pass words to the designated officers as notified by PVVNL. |

# Functional Requirements

General

- All components / systems / products used in the solution will be based on applicable national / international standards with valid certifications in place at the time of implementation of Dual Metering AMI solution, unless exempted specifically or no standard exists. In case of items for which standards are not published or not mandated, a self-certified technical specification data sheet shall be submitted along with the bid document.

- Communication media will be used in strict accordance with applicable law and adhere all regulatory guidelines (including limits of radiation prescribed for human safety) having necessary approvals in place prior to filing of bid unless exempted specifically.

- Only minimum parameters of components are mentioned, and implementation agency is expected to use better / higher specifications required for end to end metering solution, as complete system in holistic manner.

Modules

- Three Phase whole current dual registry meters with disconnection switch

- Adapter OTT Node in case meters are connected with PVVNL back-end system via optical port/ physical communication port

Dual Registry Meters shall comply with the enclosed Technical Specifications. Three Phase CT operated meter shall comply IS 14697. The supplier / manufacturer would furnish valid BIS certification at the time of implementation of Dual Metering AMI solution. The dual meter installation shall be done by the AMI Implementing Agency (AIA)/solution provider as per the rules and regulations and practices of Utility. After meter installation, customer identification no., meter ID, its hardware & software configuration, name plate details, make, type i.e. 1 Phase or 3 Phase, etc. (as per requirement of PVVNL) shall be updated in DCU/HES/MDM. The information would also be updated on the portal/app for providing information to consumers.

The AIA may offer Over the Top (OTT) Nodes to be fitted on the optical port of the newly installed meters or to be interfaced with the communication port like RS-232/ 485 of such meters.

- Communication infrastructure

The communication infrastructure should be based on RF mesh network. The back-haul arrangement between DCU and HES shall be on GPRS/ 3G/4G/nbIoT. The communication network shall be based on suitable standards from ITU/IEC/IEEE/CEN/ CENELEC/ ETSI for NAN and WAN network. Communication network shall provide reliable medium for two-way communication between meters & HES.

RF based network should either use license free frequency band available in India and / or get necessary approvals from designated authorities. The engagement of network service provider would be in the scope of AMI Implementing Agency to meet the performance level as given in the document.

Network Security

The Network shall have adequate cyber security measures not limited to the measures as described below. The network security would be extended to all the interfaces also.

- Secure Access Controls:

The system shall include mechanisms for defining and controlling user access to the operating system environment and applications. Best practices from enterprise security including password strength, password aging, password history, reuse prevention etc. must be followed for access control.

- Authorization Controls:

A least privilege concept such that users are only allowed to use or access functions for which they have been given authorization shall be available.

- Logging:

Logs must be maintained for all attempts to log on (both successful and unsuccessful), any privilege change requests (both successful and unsuccessful), user actions affecting security (such as password changes), attempts to perform actions not authorized by the authorization controls, all configuration changes etc. Additionally, the access to such logs must be controlled in accordance to the least-privilege concept mentioned above, so that entries may not be deleted, accidentally or maliciously.

·	(D) Hardening:

All unnecessary packages must be removed and/or disabled from the system. Additionally, all unused operating system services and unused networking ports must be disabled or blocked. Only secure maintenance access shall be permitted, and all known insecure protocols shall be disabled.

(E) Malicious Software Prevention:

Implementation of anti-virus software and other malicious software prevention tools shall be supported for all applications, servers, data bases etc.

(F) Network Security:

The network architecture of the HES must be secure with support for firewalls and encryption. The system shall also allow host-based firewalls to be configured, as an additional layer of security if the network firewall were to fail.

Back-end IT system and software

Dual Metering Head End System

Dual Metering Head End System is the critical interface to the field devices and is intended to interact with complete device ecosystem to achieve the desired result of dual metering in the context. It shall support Dual Meter Data Collection, support push and pull mode of data collection from meters. Other than interacting with meters for stored metering data, dual metering Head End system shall communicate with data aggregators/ concentrators, provide Network Operation Centre functionality, remote device configuration and management, remote firmware upgrades/programmable parameter inputs to network devices, send Load Curtailment signals, disconnect / reconnect, alert and alarm management and other signals. The HES should communicate with data aggregator through best suitable technology using GPRS / 3G / 4G/MPLS on private M2M APN and transporting data at DC/DR through MPLS connectivity for maintaining the data security.

HES would perform all the requisite functions as per the defined functionalities of dual  metering AMI and it will be the responsibility of the dual metering AMI Implementing Agency (AIA)/ Solution Provider to supply the requisite software and hardware to achieve the defined functionalities of dual metering AMI. Dual metering HES shall ensure data integrity checks, for example, checksum, time check, pulse, overflow, etc. on all metered data. Dual metering HES shall be based on open platform based on distributed architecture for scalability without degradation of the performance using additional hardware. HES shall support storage of raw meter data, alarms and alerts for minimum 7 days. Adequate data base and security features for storage of data at HES needs to be ensured.

UPPCL has its billing engine deployed across the state and empanelled AIA/Solution Provider should provide connectors from dual metering HES for Utility power billing data to the existing billing system and MDAS of PVVNL. Dual metering HES shall be Service Oriented Architecture (SOA) enabled.

Other Functional requirements

- Since, the Dual metering Head End System to be deployed shall collect data from peripheral devices other than meters and may release command for actuators/ relays to operate, dual HES  should have SCADA features.

- The Dual metering HES should support remote configuration of the device for different parameters as time interval for data collection, setting of threshold parameters for alert generation individually for UTILITY POWER and DG, replacement of meter, threshold for theft / pilferage identification and threshold for power quality parameters as power factor and voltage.

- Dual metering HES shall support Over the Air Firmware upgrade for network devices that may need upgradation to meet varying requirement of dual metering like Load control/ dynamic tariff implementation of availability/ generation cost based tariff.

- The Dual metering HES should maintain logs for all the events and should be capable to reproduce it on demand.

- Tampering events:

    - Must be able to detect meter / device tampering, OTT Removal, Device failure, communication failure.

    - Communication failure between Meter/ OTT and HES / Meter faulty

- Analytics based theft detection, based on data analysis/ analytics

- Dual Meter shall send all the events to the Head End system.

- If any discrepancy is found, compared to threshold parameters set by PVVNL, automatic notification shall be created for PVVNL representative or process to analyze the tampering event and take appropriate action (for example, to create a service order to investigate).

- Time Sync: Solution provider to make sure to take appropriate measures to keep all the components time synced to make sure that the data integrity is not compromised.

The functions of Dual metering HES should be:

  - Acquisition of dual meter data on demand & at selectable periodicity for both the source – Utility power and DG individually definable by DISCOM and/ or developer/RWA

  - Two-way communication with DCU if any

  - Generate signals for connect & disconnect Audit trail and Event & Alarm Logging

  - Encryption of data for secure communication

  - Maintain time sync with DCU if any

  - Handling of Control signals / event messages on priority

  - Communication device status and history

  - Network information in case more than one technology is deployed in field between the two devices

  - Critical and non-critical reporting functionality. The suggestive critical events may be alarms and event log for dual meter events like tamper/power failures etc., if data is not received from DCU/Meter, if relay does not operate for connect / disconnect or there is communication link failure with DCU/Meter or network failure. Non critical events may be retry attempts on communication failure, periodic reading missing and failure to connect etc.

MDM

The Meter Data Management System shall support storage, archiving, retrieval & analysis of dual meter data and various other MIS. It shall act as a central data repository. Dual metering MDM shall have capability to import raw or validated data in defined formats and export the processed and validated data to various other systems sources and services in the agreed format. It shall provide validated data for upstream systems such as billing, consumer Information system, customer care, analytics, reporting, Network planning & analysis, load analysis/forecasting, Peak Load Management, Outage management etc.

The Solution Provider / AIA shall specify and deliver an initial system that supports the collection and storage of data for meeting the performance level for the defined no of consumer meters (The exact Number as defined by PVVNL as per requirements with facility of future expansion. The MDM shall have the ability to selectively choose which data to be maintained and which to be purged or archived as per requirement of Utility (user selectable))

Since, prepaid functionality is being achieved through near real time data acquisition from consumer meters and Common area Power charges shall be deducted from consumer accounts on daily basis, so the data should be stored in such way that it shall be readily available for Big Data analytics and data science. The data stored shall be of time series form, which may be used for data engineering purposes.

Functional Requirements of MDM

Asset Management

- The Dual metering MDM shall maintain information and relationships between the installed meter location (society, apartment, shop address etc.), Consumer information (Name etc.), Consumer account no, Meter ID, Type of Meter (type of consumer, 1 phase/3phase, with or without relay, etc.), Meter configuration (Demand integration period, Load profile capture period etc.), GIS supplied information (longitude, latitude, connection with feeder/ transformer/ pole etc.) etc.

- The software should support tracking the status of meters and communication equipment from the date when they are installed in the field. The history of in-service asset location is maintained throughout the device life with start and end dates associated with each in-service location reference.

- Ability to report and log any damage / deterioration in the meter attributable to consumer /utility like aging and probable deviation of calibration due to ageing of meter/ infrastructure.

AMI Installation Support

- The Dual metering MDM shall also support device lifecycle management from device registration, installation, provisioning, operations and maintenance to decommissioning etc. The MDM shall generate exceptions for meters or OTT modules not delivering the correct meter data after installation.

- The MDM shall provide a reconciliation report that identifies the dual meters that have been installed but not communicating for a designated (configurable) period. MDM shall generate reports on the number of meters installed in comparison to the number of meters successfully communicating.

Meter Data

- The MDM shall accept, input, process, store, and analyze Dual Meter data from Dual metering HES and dual meter data collected through hand held meter reading instruments and manual meter reads. In case of manual reads, provision should be there to insert associated notes like assessed energy, etc.

- The MDM should accept, input, process, store, and analyze non-billing dual meter data such as voltage and power quality data (like under/over voltage, etc.) as they are available from dual metering AMI Head End Systems. The MDM should also support schedule and on-demand meter reads and pinging of meter states by authorized users and by other utility systems.

- The MDM shall provide storage of all collected Meter Data, events and alarm. It shall have capacity of storing complete contract period data or more via archiving.

- Correctly track & resolve energy usage across meter changes with no loss of individual meter data.

- Provide complete history and audit trail for all data collected from dual meters including commands sent to meters and other devices for 30 days (configurable period).

- Execute on-demand read processes.

- Handle special metering configurations like multiple tariff category at same premises.

- The MDM shall have the ability to manage at a minimum 5-minute interval data.

- Data Integrity- AMI Implementing Agency (AIA) shall ensure data integrity checks on all metered data received from data collection systems.

Data Validation, Estimation, and Editing (VEE)

The validation and estimation of metered data shall be based on standard estimation methods.

- The MDM should support and maintain following data.

  - Registered Read Data including register reads, daily billing cycle, as well as derived billing determinants like TOU

  - Interval Data channels with variable intervals and variable units of measure

  - Calculated Data that is derived or computed such as billing determinants and aggregated loads.

  - Event data storage of all collected event and alarm data from meters, network equipment, and MDMS itself

- MDM shall flag, alarm and trigger an estimating process including but not limited to when the following anomalies occur in the cumulative (“CUM”) register reads

  - CUM Decrements within a billing cycle

  - CUM reads increments more than configurable threshold

  - Future or old read dates

  - Number of digits exceeds number of meter dials

- MDM shall detect, flag, alarm and trigger an estimating process including but not limited to when the following anomalies occur in Time of Use (TOU) register reads

  - Register Decrements

  - Resets (to zero)

  - CUM reads increments more than configurable threshold

  - Future or old read dates

  - Erratic compared to CUM read (sum of TOU reads minus CUM read)

- MDM shall detect, flag, alarm and trigger an estimating process including but not limited to when the following anomalies occur in Demand register reads

  - Do not reset on cycle

  - Do not reset coincident with customer move-out or move-in

  - Reset off cycle inappropriately

  - Too high

- All data shall be transferred to billing system after meter data validation and estimation including single point meter data with respect to energy audit.

- MDM shall estimate usage for non-metered service points such as street lights, common area loads, water pump and lifts etc.

- The MDM shall maintain both the original received raw data in a non-manipulated state, in addition to VEE data.

- Notwithstanding the latency of data collection via the AMI system, once the MDM receives meter read data, the VEE process occurs in real-time and the post-VEE data is then immediately available to user or external systems.

- The MDM shall be able to automatically flag data changes from manual edits, VEE (Validating, Editing and Estimating) rules and data source corrections and electronically generate audit trail with timestamps and user-ids.

Billing Determinants Calculations

The MDM-

- If required, MDM shall allow configuring multiple TOU/TOD options (e.g. the number and duration of TOU rate periods) by customer type, tariffs and day type (weekend, weekdays, and holidays) and by season.

- Shall support the processing of interval data into billing determinants to include the following at a minimum:

    - Total Consumption

    - Consumption in different time blocks if required in the case of ToU billing

    - Maximum Demand (in kW and kVA)

    - Number of tamper counts

    - Average power factor

- Shall process interval data and frame it into the appropriate TOU periods for consumption and demand; for example, roll up 15/30-minute data intervals into hourly data.

- Shall have the ability to properly account for special metering situations such as check metering, sub metering, prepaid metering and net metering when calculating billing determinants and sending them to billing and other systems.

- Shall have the ability to properly account for special situations including, but not limited to, curtailment requests, demand response scenarios when calculating billing determinants and sending them to the billing software.

Exception Management

- Ability to capture and log data exceptions, problems and failures and to generate management reports, provide trend analysis, automate generation of service requests and track corrective actions.

- Ability to group, prioritize, filter and send system generated alarms and events to predetermined email addresses, cellular text messages to phone numbers/SMS/customer care etc.

- Exception Generation – MDM shall generate exceptions based on configurable business rules including but not limited to the following:

• Meter tamper alerts

• Communication module health alerts for Meter/DCU

• If the consumption is less/more than pre-defined average consumption

• Negative Consumption

• Power outage indications received from the Dual meter

Service Orders

- The MDM shall generate service orders based on configurable rules for various events and alarms such as stop meter, tampers, problem in communication networks, AMI host server, etc.

- MDM shall send service orders via SMS, email, etc. with the email addresses / phone numbers being configurable. MDM shall receive feedback on action taken on the service order and track the status of service orders.

Customer Service Support

- The solution shall provide customers with access to current and historical consumption and interval data, outage flags, voltage and power quality indications. The data shall be displayed in graphical and tabular form depending on user choice. The Customer may also access data through customer portal. The solution shall integrate via a user-friendly graphical interface.

- MDM shall support email/SMS notification of configured alarms & events to selected users.

- The MDM shall support the web portal or shall have the ability to interface with the 3rd party portal/utility portal to provide the consumer near real time online views of both usage and cost and helping consumers to understand electricity usage and cost information, alerts and notifications and energy savings tips with different levels of detail. The portal should support the view for past electricity usage, last week’s, yesterday’s, current days or other period etc. as per selection.

The portal should provide user friendly access to consumer for their data via colorful graphs and charts and can download the data into a spreadsheet. It should support mobile app through which consumer shall be able to log in through android/iOS based mobile app to see information related to his energy consumption.

Analysis

The MDM shall have analysis capability based on configurable business rules including but not limited to the following:

- Display consumption/load profiles by configurable period (15/30 min, hour, day, month, year etc.) day type (weekday, weekend, holiday, festival wise etc.) and by tariff, customer type, or any user specified collection of meters.

- Generate peak & off-peak load patterns by aggregating all loads of consumer group.

  - Perform building complex/ tower/ feeder wise energy audit.

  - Perform load analysis for different groups and categories of consumers.

  - Ability to provide the data to load forecasting, load or demand response applications and perform error management like: Missed reads and intermittent meter reads before taking into forecasting, load research or demand response

- Ability to configure the system to effectively visualize consumption trends, identify unusual patterns, and visualize load analysis to understand which assets are being over utilized.

- Analyzing data to identify new patterns of usage, transformer overload alerts / demand – supply gap alert etc.

- Ability to receive and store outage and restoration event data from meters and outage systems and to log all such events for analysis.

Reporting

The solution shall include a list of the standard reports that are provided with the MDM including but not limited to following:

- Daily data collection report

- Usage exceptions

- VEE validation failures

- Missing interval Read date and times (on hourly, daily, weekly & monthly basis)

- Physical meter events (install, remove, connect, disconnect) & meter reset report

- Meter flags

- Meter inventory

- Defective meters

- AMI performance measurements

- Threshold Exception

The solution shall support users modifying standard reports to better meet specific reporting requirements.

- The MDM shall enable the Utility to deliver reports in standard digital format such as PDF, Excel, etc.

- Ability for GUI (Graphical User Interface) to set up or change report delivery to configurable email addresses, network file directories, ftp sites or printer systems without modifying source program code and without any proprietary language skills.

- All queries shall be generated through user driven drop-down menu in GUI.

The empanelled agency shall provide example queries to support internal report generation needs.

- Ability to provide daily & weekly interface exception reports between MDM and other subsystems e.g. billing, outage, etc.

Revenue Protection Support

- Ability to analyze power outages, usage trends and usage profiles to identify potential energy diversion situations, and produce daily reports, monthly reports and service order requests for investigation.

- The business rules for revenue protection alerts shall be configurable via user-friendly interface.

- The MDM shall filter out revenue protection alerts that may be caused by field activities if the field activity information is provided to the MDM.

- The MDM shall support the analytics/investigation (i.e. view current and historical usage patterns) to valid suspected revenue protection issues.

Demand Control / Demand Response Support

AIA shall describe how its MDM supports Smart Utility power Demand Response programs involving Demand Response (DR) systems as part of PLM. The solution shall support the following analysis:

- Totaling the actual consumption during the DR event.

- Totaling the actual consumption of different groups that participated in the DR event.

- Comparing the actual to baseline consumption for the groups in above.

Outage Management System (OMS) / other smart utility power functionality support

MDM shall support OMS system as per the requirement of the utility.

Prepaid functionality

For achieving prepaid functionality, the system should have the following capabilities for Utility power and DG supply:

- The MDM should support pre-payment metering and capability to interface with pre-payment application of Utility and RWA Revenue Management System.

- The prepayment should support the system that payment and connection parameters are stored centrally, and the details are being updated to consumer portal/ app.

- The system should periodically monitor the energy consumption of prepaid consumer and decrease the available credit based on consumption.

- The system should send connect/disconnect command on the basis of available credit as per notified rules & regulations.

- The system should send low-credit notifications to the consumer when their balance approaches a threshold. The threshold should be definable by user and should have provision for defining different threshold for Utility power and DG.

- The system should support online / coupon-based mechanisms for recharging.

Interface (Web/Mobile App)

User Interface

The AMI Implementing Agency (AIA) shall provide user interface for the following:

Utility

User interface for utility shall have ability for at least the following functionality:

- Display meter data at a user defined configurable cycle through a GUI that allows authorized users to view energy usage patterns and the data behind them for selected customers.

- Compare multiple multi-story facilities against each other based on costs, average spend, and cost by weather.

- Allow authorized users to view metered data, initiate and view reports, modify configurations, and initiate and update service requests via a GUI.

- Display via a GUI the energy usage profile for a single meter or group of meters. The load profile shall illustrate energy consumption and peak demand in user defined intervals for a user-specified time period.

- Access to historical energy usage and meter reads through the GUI.

- GUI to clearly and visually distinguish between metered, estimated, allocated and substituted data.

- GUI to provide role-based access based on user identity and user role. Shall have following types of users:

o Administrator

o Operator

o Field staff

o Viewer/Guest

- Ability for utility through user interface to set up alarm and event notifications that can be directed to a combination of configurable email addresses, cellular text messages or phone numbers.

- User interface for utility to update the credit amount of prepaid consumers to MDM. Such type of user interface before login shall require password & login-id. For authentication. User interface after getting information like consumer i.d., mobile number & recharge amount etc. shall update the same to MDM. The details of payment information shall also update to consumer through SMS, email etc.

Consumer

User interface for all authorized consumers shall have ability for at least the following functionality:

o View metered data, initiate and view reports

o Can make request for connection/disconnection

o User can update mobile number/email

o Can initiate service requests for maximum demand updating, meter checking etc.

o Consumers can view recharge history & present balance.

O Recharge their account by logging on user interface. User interface shall require consumer id., mobile number & password for secure login. This user interface shall be integrated with the present online payment gateway of utility.

Integration with other Systems

MDM shall preferably interface with other systems on standard interfaces and the data exchange models and interfaces shall comply with CIM / XML / IEC 61968/IS15959/ Indian Companion Specification/ any other open standard. MDM solution shall be Service Oriented Architecture (SOA) enabled.

MDM integration with other systems shall include but not limited to the following:

- Dual metering HES for data exchange from other AMI solutions

- Utility Administration

- Existing other Data Collection Systems

- IVR system, CRM, Consumer Portal

- Billing and collection system

- GIS Systems integration with MDM system

- Support of interface with HHU or manual reading system etc.

- RWA Revenue Management System (with limited data sharing with respect to DG Supply only)

AMI Implementing Agency (AIA) should provide suitable number of HHUs to read and update the data in MDM in case of any communication failure between meter and HES/MDM.

Performance Levels/ Service Level Agreement (SLA)

(a) These performance levels shall apply to the complete Multi-Point AMI system.

(b) AMI system includes the communications links provided by Network Provider /third parties such as telecommunications companies and AMI Implementing Agency (AIA) has to ensure the desired performance level.

(c)The performance levels are average performance levels over the period of a year and exclude force majeure events.

The following are the required performance levels

Performance levels for collection of daily meter readings

The following are the performance levels required for the daily collection of the previous day’s interval energy data and total accumulated energy:

(1) All interval data from 95% of meters within 8 hours after midnight; and

(2) All interval data from 99.9% of meters within 24 hours after midnight.

(3) In the event if data of a meter is not received beyond 24 hours, on occurrence of such event beyond 4 times in a month. FMS charges of respective meter shall not be paid to Service Provider.

Performance levels for remote reads of individual meters if data is not received on daily basis

The performance level of an individual read applies to the collection of seven days of interval energy data and the current total accumulated energy from a particular AMI meter whose data is not being received on daily basis. The performance level required shall be:

(1) Action performed at 90% of meters within 1 Hour;

(2) Action performed at 99% of meters within 2 hours; and

(3) Action performed at 99.9% of meters within 6 hours.

Performance level for remote load control commands for selected consumers,

The performance level required for individual meters shall be:

(1) Action performed at 95% of meters within 3minutes;

(2) Action performed at 99% of meters within 5Minutes

Performance level for remote connect/disconnect for selected consumers,

The performance level required for selected individual meters shall be:

(1) Action performed at 90% of meters within 2minutes;

(2) Action performed at 99% of meters within 3 minutes; and

(3) Action performed 99.9% of meters within 5 minutes.

Performance levels for meter’s failure to register energy as per energy source

Alarms to be received within 5 minutes.

Performance levels for updating of data on consumer portal/ app

The performance level of updating of individual consumer data on portal/ app after receiving the data in MDM shall be:

(1) Action performed for 90% of consumers within 15 minutes after receiving the data in MDM;

(2) Action performed at 99.5% of meters within 30 minutes after receiving the data in MDM.

Performance levels for resolution of disconnection related issues

(1) Software related issues to be resolved within 1 hour

(2) Other issues to be resolved within 8 hours.

In case of default to above FMS Charges of respective meter will not be paid.

Performance levels for replacement of defective meters

- Meter should be replaced within 3 days. In case of default monthly FMS charges of that meter will be deducted.

Remotely top-up amount

| Delivery of top up amount/ credit recharge in case of prepayment post successful transaction from payment gateway up to consumer interface (command from HES) | 99.9% meters within 30 minutes (delivered and intimated to consumer) |
| --- | --- |

System Availability

| Availability of AMI System per month | ≥99.5% |
| --- | --- |

The performance level for generation of bills would be as per requirement of the utility. The performance levels regarding meter discovery time line after installation, on demand reading of meter data for operational purposes, outage restoration enquiry response time etc. would also be as per requirement of the utility.

Service Provider shall submit AMI generated reports for cases mentioned above based on data available in HES.

Penalty for non achievement of Service Level Agreement (SLA)/ Performance Level

- Beyond the minimum performance level as mentioned above for each 1% there shall be penalty of 0.50% of monthly FMS charges.

- The total penalties under SLA categories are capped at [30%] of FMS Charges. Service Provider shall ensure that the data collection and computation for the purpose of SLA penalties (as mentioned above) should be automated and visualized in PVVNL/Officials Interface.

Technical Obsolescence

The systems including communication technologies, which are at a risk of technical obsolescence over the next few years and over the operating life of the system should be identified and reported. This may also include end–of-sale and end-of-support policies governing the proposed technologies. The compatibility between the various elements of the system need to be considered and mitigation options, not be limited to periodic update from OEM /System supplier, shall be indicated in detail.

Description of system architecture

| SN | Function | Requirement |
| --- | --- | --- |
| 1 | Provision of an integrated system of hardware and software to meet the required functionality | An integrated system should be provided to meet the following functional requirements: - - Real Time data acquisition from Dual Source Meters as per configurable time interval. - Supervisory function i.e. processing, monitoring, analysis and diagnostics - Data exchange between various devices installed in the distribution network for rule-based actions. - Storage of data - Facility for user defined forms and reports - Facility for RTC management - Alarm list - event list - Parameter Limit value violations - Configurable interval for acquiring energy accounting data - Prepaid Functionality for Utility power and DG supplies - Bifurcation of captured data to cleanly handle Utility power data through PVVNL IT systems and DG data through implementation agency / RWA IT systems with full isolation and integrity. |
| 2 | Flexible deployment / implementation of system | The system deployment/implementation should be flexible and modular. PVVNL should be able to implement different solutions in different areas depending on specific requirement. For example, initially it may opt for all the essential functionalities covered in the scope of work and subsequently for some optional functionality as described in Scope of work may also be considered without any interface issues with the existing system. Also, the deployed system should be upgradable without requiring any hardware replacement except meters. It should be understood that for the back-end IT system, field device interface point is DCU. The DCU offered shall act as a neutral communication middleware and should seamlessly interface with existing as well as future field devices, dual registry meters of different makes. To cater to this requirement, DCU offered should have spare communication ports/ physical interface point for integration with different communication medium such as RF mesh, Zig-bee, Wi-Fi, PLC etc. |
| 3 | Intelligent middleware/ end points | The middleware/ end point devices should be capable of FOTA (Firmware over the Air) and OTA (Over The Air) upgrade. There should be no requirement of change of hardware with change of smart meters/ static meters. |
| 4 | Provision for push and pull plus remote and local data collection | The system and devices should work on push and remote mode of data collection i.e. the system shall support configurable time interval for devices to push dual meter data automatically to the head end. The system should also support on demand data (pull) by the Utility and also collection of data through a local terminal through RF communication. |
| 5 | Facility for Web based front end | Software shall have web based front end. |
| 6 | Provision for flexibility, user friendliness, scalability & Security | The software system shall be flexible in terms of System & Application software. The software should have necessary features to maintain audit trails with complete event logging. The software shall have multi-level configurable password control for data protection, integrity and security of the system. The different software features shall be protected by different passwords. All configurations of User Management / Access Rights shall be as per the requirements of PVVNL. |
| 7 | System with robust architecture, high availability and reliability | The system should be based on a robust architecture model / framework that is highly scalable/ available/ reliable, gives good performance, and offers distributed computing. The AMI database servers shall be enterprise level 64- Bit processor-based system and should be capable for fully populated configuration of database related to Minimum 1 million consumers. |
| 8 | API Layer | The API Layer will be the interface of the head end with the utility’s operations / dashboard user. The API will provide the entire user interfaces for the operational and supervisory activities involved in meter data acquisition, processing and analysis. |
| 9 | Automatic workflow process from data acquisition to analysis | Normal workflow processes from meter data acquisition to analysis would be as automated as possible; for example, user intervention would be sought only for data editing or verification decisions. |
| 10 | Database | The database should comprise of an RDBMS that should be designed to be able to maintain the relationships between meter and network assets, network topology, user privileges, service points, customer accounts and other entities. |
| 11 | Maintenance of time stamped database | The database should also maintain a time- series repository that stores the data collected and processed from meters, including interval usage data, event logs and outage history, as well as derived data such as aggregations and asset performance indicators like load factor and load duration curves. |
| 12 | Optimal designing of database | The database tier should be optimally designed to exploit both normalized as well as multidimensional data models. |
| 13 | Network Architecture | Group of Consumer meters will communicate with the Data aggregator installed at suitable locations either in meter rooms/ floors/ buildings. These data aggregators will communicate with data concentrators on RF communication. Data concentrators/ aggregators / Consumers meters will form a RF mesh with proper security mechanism in place. Bi-directional communications between Gateway and Head End System should be achieved in following way: - - Communicatio protocol between Gateway and dual HES shall be based on TCP-IP (IPv4/IPv6) - Gateway hardware and Head End System must support IPv6 - Dual Meters to Data aggregator over control wiring. - Data aggregators to data Concentrator Unit (DCU) over RF Mesh. This will form the Neighborhood Area Network (NAN). - DCU to be Installed at each building or as per requirement of frequency of meter data reads for effective implementation of centrally controlled prepaid electricity system.. This may be part of the RF NAN/ or can have GPRS/3G/4G SIMs. - DCU/ Gateway to dual metering Head-End System (HES) over 4G with fall back to 3G/2G/ GPRS on private M2M APN. This will be the part of Wide Area Network (WAN) The RF network should support full mesh topology to ensure that there are no dark spots in the network. |

Acceptance Testing Criteria (primarily for PVVNL related Utility power Data)

The acceptance testing criteria mentioned herein shall be applicable for declaring successful commissioning of AMI system. The bidder shall be required to get the independent witness test done at their own cost by NABL accredited lab of repute for first site before acceptance  by DISCOM.

| SN | Function | Test Procedure | Desired Result |
| --- | --- | --- | --- |
| 1 | Type of Consumer Meters- Dual Register three phase meters as per IS 13779 | Type tested from a lab of repute, BIS certified and IS-13779 marked | Change of energy meters from existing to the meters of empanelled meter manufacturers. No change of single point HT meters |
|  | Type of single point HT/ LT Meters – Static Energy Meters as per IS 14697 standards | No change in the deployed energy meters (with optical port) is allowed. The solution should be deployed on the current energy meters with optical port. |  |
| 2 | Mode of Interface - Optical or RS232/485 | The device to be installed at the meter should interface with the meter through Optical Probe or RS232/485 port available at meters. |  |
| 3 | NAN (Local/Neighbourhood Access Network) | The NAN network has to be setup on RF-865 MHz mesh network i.e. all consumer meters within a complex need to communicate with the DCU on RF-865 MHz mesh network. There should be no loss of data. The availability of the data will be verified at the backend. Minimum 99% of the data should be available over a period of 15 days. | No Loss of data. The availability of meter data will be verified at the back-end, the minimum criteria is 99% over a period of 15 days i.e. if the read interval is 5 minutes then a total 4320 readings should be taken in 15 days and to achieve the success criteria a minimum of 4276 reading per meter should be available at the backend. |
| 4 | Web Based Interface | All the testing, setting of parameters, viewing of report & notifications, configuration, collection of meter data should be available through Web Interface. The Web Application should have different access level i.e. facility to create users with different access rights. Multiple login (Minimum 10 users) should be available. | Successful execution of the AT through Web Application. |
| 5 | Automatic Meter Reading of consumer meter and single point meter | The meter reading of all the meters will be physically verified with the readings available at the head end system. This testing will be done in the field through the Web Application. The meter reading interval should be programmable in multiple of 5 minutes with minimum interval as 5 minutes. | 99% readings with timestamp should be available at the backend |
| 6 | Outage Detection and switching of meter register for Utility power and DG | The Utility supply at single point meter will be disconnected and it will be verified that the system provides the information at the backend with proper time stamp. DG will be started. Consumer meters to record energy consumption during DG run period in DG register. Online dashboard to provide DG running status. The system should provide the information with time stamp. The Utility Supply will be restored, and the system should provide the information with time stamp. While supply is on Utility power, DG will be started. No consumer/ common area meter should record consumption in DG mode. While supply is on Utility power, DCU shall be switched off. After 15 minutes, DCU is switched on. Consumption data should come at the back-end as recorded in the meter. The time of disconnection and restoration will be verified in real time i.e. through the Web Application and through the outage report generated by the system. The switch between Utility power and DG should happen accurately and reliably with consumption recording in respective registers and displayed through the web interface of utility and / or RWA Revenue Management System. | 99 % accuracy in outage reporting i.e. out of 200 such events minimum 198 should be accurately reported. The Web application should provide information of outage in near real time (maximum permissible delay is 120 seconds) |
| 7 | Power Quality Parameters - Monitoring of Voltage, Power Factor, frequency and current | PVVNL will set the threshold limit for High and Low Voltage alerts, Low Power factor alerts, High & Low Frequency alerts and High Current. The system should generate alerts in real time if any of these limits are breached. The limit setting will be done from the backend i.e. through Web Application. The provision to disable alert for any of the parameters should also be available. | 99% of the alerts should be recorded. The threshold limits of different parameters should be changed through the Web Application, as below: - Voltage High and Low - PF low - Frequency High and Low - Current High Alerts should be deactivated through Web Application |
| 9 | Load Management - Restricting the consumer load to contracted limit | PVVNL will set the load limit of consumer if the load being consumed exceed the contracted load the system should disconnect the supply of the consumer. Different Load will be set for different consumer. Also, the system should work in alert only mode i.e. the provision to disconnect will be disabled but if consumer exceeds load, appropriate alert should be issued. The load setting can be done either in kW or in kVA | Disconnection of consumer on exceeding load and issue of proper alert message. Change of contracted load of consumer from backend. No disconnection, alert only mode |
| 10 | Remote Disconnection | PVVNL through Web Application, will disconnect the supply of consumer | The consumer supply should be disconnected, and the supply should not be available to consumer. |
| 11 | Prepaid Functionality – Automatic Disconnection and Reconnection | The consumer supply should get disconnected if his account balance is exhausted, taking into consideration any grace amount if applicable. The system should disconnect the consumer if the recharge amount is consumed and the supply should be restored on recharging the consumer. This will be done through web application. There should be a functionality to reconnect the consumer without recharge also. | Successful disconnection and reconnection of prepaid feature through web application. This should work equally well for Utility power and DG supply. |
| 12 | Energy Audit Data in kWH | This functioning is achieved by collecting the kWH reading of all the meters, in a complex, within a span of 4 to 5 minutes i.e. if energy audit is required for 12:00 HRS then all the meters should be read from 12:00 HRS to 12:05 HRS. The energy audit interval will be programmed from the backend. The minimum audit interval should be 6 hours i.e. 4 energy audit data point per day. The energy audit start time should also be programmable. The Audit reports will be physically verified for its accuracy. | The meter reading for all the meters, for audit function, should be within a span of not more than 5 minutes to maintain the accuracy of the audit. All the data should be available with time stamp. |
| 13 | CAP power deduction mechanism | The electricity consumption(energy charges) and demand charges(fixed charges) of common area supply to be deducted on daily basis through prepaid account balance of individual consumer apportioned according to contracted load of the consumer. | The Energy difference of the reference meter & cumulative consumption of meters of individual consumers shall be apportioned according to the contracted load of the individual consumers having electricity connection in the M.S. building. Software should have the feature to implement this mechanism. |
| 14 | Change of Meter | Two to three meters (already integrated on the system) will be changed and the change will be updated on the system through web application. On committing the changes, the system should start collecting the data from these meters. No hardware change is allowed. | Successful integration from backend without changing the hardware at the customer premises or visiting the customer premises. |
| 15 | Alert / Event Notification | The AT Officer will test for the following alerts - Device Tamper i.e. opening the meter box - Device not communicating on Optical probe removal (in case of (OTT) | 99% of the alerts should be recorded. |
| 16 | Network Monitoring Centre | All the devices should be centrally monitored from a NOC and the deviations should be updated on NOC in real time | Availability of NOC monitoring system |
| 17 | Localized Intelligence - Functioning of critical functions even in absence of backend connectivity | The connectivity of Gateway / Data Aggregator at the DT will be disconnected from the backend system. The following functionalities will be tested: - - Disconnection of consumer on High / Low Voltage and power factor - The customer should be disconnect on exceeding the contracted load | 99% accuracy |
| 18 | On demand reading | Though the system is fully automated, but provision to pull the meter data should be available. PVVNL AT Team will test by issuing on demand commands from the web application. | 99% success rate of on demand reading |
| 19 | Firmware Over the Air (FOTA) | The solution should support firmware upgrade over the Air. The solution provider will be required to demonstrate. For example, a different make meter shall be placed by removing existing meter. From Back-end through FOTA, the meter should be read without change of OTT hardware. | Same OTT should work with the new meter and the data should get successfully read. |
| 20 | Consumer Application | The AIA will provide a consumer application smart phone through which the consumer, on keying in his/her login credentials, is able to view all the meter parameters as reading, voltage, current, power factor, load with time stamp. The user interface should also be available on Web. | The users should be able to monitor their meter data |
| 21 | Integration with existing billing | The data should be in real time available either through online API or in downloadable file format that can be directly exported to billing system. | On demand availability of billing data without requiring any mediation layer for all types of meters. The data for different types of meters should be available in common format required by the billing system. |
| 22 | Integration with existing systems | The solution should provide XML / SOAP/REST based interfaces to integrate with existing or future system of PVVNL | Successful demonstration of functionality. |