TENDER SPECIFICATION OR MODALITIES OF CARRYING OUT THE WORK

- Dual metering system for GRID and DG must be fool proof. Robustness of this shall avoid any confusion with RWA and DISCOM in future as discrepancy in this data may lead to litigation.

- In Meters UPPCL supply register should be in default mode for registration of power supplied to customers. Generator (DG) mode should be triggered when generator supply is being fed into electrical distribution network.

- The meters are to be as per BIS approved standards with additional features needed for Dual metering as per relevant IS are mandatory.

- The meters used should have in-built disconnection facility as well communication network.

- There must be arrangements of prepaid recharge coupon facility as per tariff / Hon’ble UPERC guidelines for GRID supply. DG data shall be provided with secure FTP location with access rights to concerning RWA/Developer/Builder for further process.

- GRID recharge coupon needs to be integrated with LICENCEE revenue management system. All integration must happen with automated processes.

- DG tariff is to be decided by RWA, hence DG revenue management system to reside outside of LICENCEE data center/server. LICENCEE to provide only DG consumption data to outside server.

- DG revenue management, collection on post-paid / prepaid shall be choice of RWA/ Builders. Any amount pertaining to DG meter data shall accrue to RWA account. LICENCEE shall not have any intervention in this system.

- Energy accounting shall be done by LICENCEE for GRID supply only. Energy accounting for DG shall be done by respective RWAs.

- Single point bulk meter data and data of all consumer meters shall be used for energy audit in an automated manner to detect any pilferage of electricity at building level.

- While as per meter data received service provider shall process Grid readings as per UPPCL/ Hon’ble UPERC established practices like billing, disconnection, and load control, etc., and for DG data, RWA shall be free to implement their own mechanism.

- For transparency and to avoid any issues related to Grid / generator power consumption issues and charges being deducted for common area power, a real time mobile based application as prevalent in these buildings should be adopted.

- Service Provider will deploy, Manage, Maintain, AMI Network at building level do energy audit on daily basis. The server used for this purpose shall be exclusive and shall be integrated with PVVNL billing server.

- Service Provider need to provide centralized monitoring system capable of generating alerts, reports etc. as desired by PVVNL including deployment of server as well as can maintain uptime or server as per Utility defined SLA.

- Empaneled service provider to be capable of integrating/providing data of PVVNL supply to PVVNL billing system in desired formats and should integrate with PVVNL Billing system. The server will be used only for billing purposes of PVVNL.

- Empaneled service provider needs to execute tripartite agreement with PVVNL and builder/developer/RWA before starting the work.

- Empaneled service provider needs to supply, install, and commission all the equipment required for secure communication and other necessary equipment.

- Empaneled service provider shall undertake the operation and maintenance of complete AMI (Advance Metering Infrastructure) System for contract period. The operation and maintenance charges will include replacement of defective equipment/material supplied by the service provider, carrying out regular and periodic field activities required for ensuring proper health of the deployed infrastructure etc.

- The Service provider shall also provide adequate manpower 24×7 to maintain the system for contract period from the date of successful installation and commissioning of the multi point system.

- Common area electrical charges to be calculated based on given guidelines/logic on daily basis.

- The quantity mentioned in the price bid is tentative which can up vary to 50% (increase/decrease) as per actual requirement.

- The empanelment for the above work shall be reviewed every year based on the performance of Facility Management Service provider. PVVNL reserves the right to empanel other Facility Management Service provider as per the requirement & the prevailing conditions.

- The meters need to be dual source dual register preferably as per IS: 16444 or IS 13779 with IS 15959 DLMS support along with separate disconnection functionality for Utility or DG supply.

- The energy meters shall only be purchased from the vendors approved by PVVNL. Service provider must get approval of GTP of Meter & hardware.

- Vendor must submit test report of hardware other than meter as per relevant IS & IEC protocol conducted at NABL accredited Lab.

- For Meter, the Bidder has to get GTP and Vendor approved from PVVNL. Documents required for it are standard documents as BIS License, ISO Certificates, technical specification, Drawing, Past supply experience with Govt./Power sector utilities, Manufacturing details, NABL accredited LAB Certificate, Type test reports as per IS etc. The type test reports/certificates/records for all type tests specified having been successfully performed on the type of meter offered shall be submitted at the time GTP & vendor approval.

- Type Tests:

The Energy meter offered shall be fully type tested on the cost of supplier/Service provider at any of the test laboratories mentioned below by the bidder as per relevant standards, sample for type test shall be selected from first slot of supply.

Till the successful completion of type test at Lab, service provider will neither use the meters for installation on consumer premises nor any payment will be done against this supplied lot of meters. In case of getting Test lab report not as per standards then meter supplying firm has to take back all the meters of that lot on its expenditure.

1.	NPL, New Delhi

2.	ERTL (N), New Delhi

3.	ERTL (W), Mumbai

4.	ERTL (E), Calcutta

5.	ERTL (S), Thiruvananthapuram

6.	E.R.D.A., Vadodara

7.	C.P.R.I.

- Acceptance Test:

All acceptance tests as stipulated in the relevant standards shall be carried out by the supplier in the presence of the purchaser's representative.

- Routine Tests:

All routine tests as stipulated in the relevant standards shall be carried out and routine test-certificates/reports shall be submitted to inspecting team and placed inside individual meter packing.

- Surge Test:

The offered should be capable to withstand surge immunity test as per IEC 62052-11 2003 and amendments thereof. Bidder shall have to submit type test report along with offer for this test also.

Testing Meters in each lot:

Sample meters shall be selected from each lot as per IS and these meters shall be tested at one of the Third-Party Govt. Lab decided by the Discom on the cost of supplier/Service provider and its place shall be decided by the Discom, in presence of UPPCL/DISCOM authorized representative / firm’s representatives.

However, place of sample testing will be at the discretion of UPPCL/PVVNL

- Final Acceptance Testing of meters:

- Testing of meters will be done at CPRI Lab only.

- On offer of meter inspection by the meter manufacturing firm an inspection team of minimum two officers conversant with meter from the Discom will be formed which will select the meter samples randomly from the meters offered for inspection as per clause no H2.1 of Annexure H of IS.

- Inspection team will seal the sample meter in their presence and will clearly note down the meter & seal number in their sealing certificate. Inspection team will get the sealed meter samples enclosed in packing in such a way that there is no way of tempering the samples in their presence. Inspection team will mention on their sealing certificate serial number of each seal with their specimen signature, and this will be mentioned in inspection report.

- Meter manufacturer will be fully responsible for payment of all expenditure involved in delivery of the sealed and packed meter samples to CPRI lab by Inspection team, bringing back and all kind of testing charges.

- CPRI lab will test all the Acceptance Test on sample meters as per IS 13779 (With all latest amendments) in which following process is mentioned-

H-1 LOT

H- 1.1 In any consignment, all the meters of the same type and rating manufactured by the same factory during the same period shall be grouped together to constitute a lot.

H- 1.2 Sample shall be tested from each lot for ascertaining the conformity of the meters to the requirements of specified acceptance test.

H-2 SCALE OF SAMPLING

H- 2.1 The number of meters to be selected from the lot depends upon the size of the lot and shall be in accordance with Table 26.

| Table 26 Sampling Plan |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Lot Size | N 1 1 | N 2 2 | (N1+N2) | C1 | C2 |
| 1 | 2 | 3 | 4 | 5 | 6 |
| Up to 300 | 8 | - | 8 | 0 | - |
| 301 to 500 | 13 | 13 | 26 | 0 | 2 |
| 501 to 1000 | 20 | 20 | 40 | 0 | 3 |
| 1001 and above | 32 | 32 | 64 | 1 | 4 |
| 1) Size of the first sample. |  |  |  |  |  |
| 2) Size of the second sample. |  |  |  |  |  |

H-2.2 The meters shall be taken at random from the lot. The procedure given in IS 4905 may be adapted.

H- 3 NUMBER OF TESTS AND CRITERIA FOR ACCEPTANCE

H- 3.1 Test of No-Load Condition and Starting Condition

A sample of N1 meters selected according to col 2 of Table 26 shall be tested for the above tests. Any meter failing in any one of these tests shall be considered defective. If the number of defectives found in the sample is less than or equal to C1 the lot shall be considered to be conforming to these tests. If the number of defectives is greater than or equal to C2, the lot shall be considered as not conforming to these tests. If the number of defectives is between C1 and C2, a further sample of N2 meters shall be taken according to col 3 of Table 26 and subjected to these tests. If the number of defectives in two samples combined is less than C2, the lot shall be considered as conforming to these tests, otherwise rejected.

H1- 3.2 (i) Tests of insulation resistance, (ii) AC voltage tests, (iii) Test of power consumption, (iv) test of meter constant/registration. (v) limits of error and interpretation of test results and adjustment (if required).

From the sample of meters which have been drawn according to H-3.1 and those that have passed all tests of H-3.1. A sample of 8 meters shall be tested, all of which shall pass for conformity to these tests. If any of the meters fails in any of these tests, the whole lot shall be declared not conforming to the requirements of these tests.

H- 3.3 Tests for Repeatability of Error

Above tests shall be carried out on 3 samples selected from above 8 meters under H-3.2 and shall be tested for repeatability of error tests separately. If any one of the meters fails, the whole lot shall be declared not conforming to the requirements of these tests.

H- 3.4 The lot shall be considered as conforming to this specification, if provisions of H-3.1, H-3.2 and H-3.3 are satisfied.

- All tests other than which are not performed by the CPRI lab will be performed by Inspection team of Discom as per approved GTP/standard technical specification for dual source dual register 2 way communicable meters issued by UPPCL/DISCOM at the meter manufacturer works.

- Till the successful completion of type test at CPRI Lab, service provider will neither use the meters for installation on consumer premises nor any payment will be done against this supplied lot of meters. In case of getting CPRI Test lab report not as per standards then meter supplying firm has to take back all the meters of that lot on its expenditure.

- If during inspection by Inspection Team or Type Test performed by CPRI are not found conforming to technical specification or relevant IS following penalty will be imposed on the service provider-

| Case | Failure | Penal Action |  |  |
| --- | --- | --- | --- | --- |
|  |  | Replacement | Financial Penalty | Debarment from business/ Blacklisting |
| Failure-1 | 1st time failure in fresh lot | 100% | NIL | NIL |
| Failure-2 | 2nd time failure in subsequent lot or replaced previous lots of same PO | 100% | 10% of the ex-works (including F&I) value of the lot plus GST. | NIL |
| Failure-3 | 3rd time failure in subsequent lot or replaced previous lots of the same PO | Not Allowed | NIL | Debarment/ blacklisting of meter manufacturer from business in All DISCOMs for 1 year (+) |

- Performance Guarantee for the above project shall be 3% of contract value for the full contract period with additional 06-month claim period.

- Empaneled service provider must provide the cloud-based solution. Service provider should use MeitY empaneled cloud service provider. Empaneled service provider must comply to all cyber security as per guidelines of govt. and CEA. Service provider should also get certification of Solution through CERT-In approved vendors.

- Bidder has to give detailed proposal of technical solution with overall architecture, cloud solution and specification of offered equipment.

| S. No | Description | Details |
| --- | --- | --- |
| 1 | Period of Contract | - Period of Contract: Contract period for the work of Facility Management Service shall be for period of 5 years from the date of go live, which can be further extended further on year-to-year basis based on performance & mutual consent. - Delivery & Implementation Schedule: Hardware delivery, installation, commissioning, and go-live period for Completion is 6 months. Installation of hardware & commissioning shall be done Society wise and shall be completed as per timelines of Supply Code. Go-live shall be done society wise. |
| 2 | Warranty of Supplied hardware | Warranty period of supplied hardware shall be 5 years from date of commissioning & go-live. |
| 3 | Performance Bank Guarantee | 3% Performance Bank Guarantee of contract value including GST has to be deposited in form of BG for full contract period or 5 year whichever is higher with additional 6 month claim period. |
| 4 | PAYMENT TERMS | Delivery, Installation & Commissioning: Hardware other than Meter; 50% on installation & go-live of Hardware (of a Society based on occupancy). 40% on installation & go-live of meters. 10% after 3 Months of go-live of meters. Meter; 80% on Installation & go-live of meters. 20% after 3 Months of Installation & go-live of meters. Facility Management Service: Monthly payment against raised invoices of FMS Service. The services shall be evaluated against the uptime and frequency of data provided at set interval as per SLA conditions /performance level of the tender. Other terms and conditions related to supply, execution of works and payments shall be as per laid down procedure of PVVNL. |
| 5 | PENALTY | Delay in delivery & implementation of Project The implementation of the solution will have to be completed within the stipulated timelines. Failure to comply with the time frames for implementation shall attract penalty as follows: - S No; Parameter; Penalty; Ceiling. 1; Adherence to milestone timelines; If the implementation is delayed beyond awarded time, the payment to bidder will be liable for deduction as penalty @ 0.5% of respective implementation cost per week, or part thereof.; 10% of the total implementation cost. |
| 6 | EXIT PLAN CONSEQUENT TO TERMINATION | The Exit Plan should cover at least the following: - Handover all source/developed codes, related documentation, and other Configurable Items, if any in his possession. - Handover the list of all passwords at all locations to PVVNL. - Handover of all Hardware /equipment at all locations to PVVNL - The System Integrator/SSIA and the Authorized Personnel from PVVNL will sign a completion certificate at the end of successful completion of the Exit Plan. - Detailed coverage of Exit Plan shall be as per RFP Proper handover will be done to another appointed SIA/Service Provider. |
| 7 | SERVICE LEVEL AGREEMENT | Performance Level will be applicable as per “6. Implementation Guidelines”. - Beyond the minimum performance level as mentioned above for each 1% there shall be penalty of 0.50% of monthly FMS charges. - The total penalties under SLA categories are capped at [30%] of FMS Charges. Service Provider shall ensure that the data collection and computation for the purpose of SLA penalties (as mentioned above) should be automated and visualized in PVVNL/Officials Interface. |