## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : fo¦qr uxjh; forj.k [k.M & f}rh;] uks,Mk ds vUrxZr vfrHkkfjr ifjorZdksa dh vfrHkkfjrk nwj djus gsrq dqy 13 ua0 u;s ifjorZdksa dh LFkkiuk ls lEcfU/kr dk;ZA
Contract No: SHORT TERM E-TENDER NO 68/EUDC-II NOIDA/2023-24
G.S.T. AND ALL TAXES INCLUSIVE IN ALL QUOATED RATES.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) The rate quoted by the tenderer shall be inclusive of all duties, taxes (except GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. GST AND ALL TAXES INCLUSIVE IN QUOTED RATES. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder INCLUSIVE OF ALL TAXES AND GST Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with All Taxes and GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Installation of New Distribution Transformer against overloaded transformers in under EUDD-II, NOIDA. (DETAIL OF WORK MENTIONED IN TENDER FORM) | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe carriage of following stock material, from any of the Store Center of PVVNL to work site including Loading from Store and safe unloading at site for Item No. 3 to 8 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | 400 KVA T/F 11/0.4KV |  | 1 | Nos. | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | 11 kv Pin Inulator with Pin &Nut |  | 1 | Nos. | 100 |  |  | Excess(+) | 99 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | ST Pole 11 Mtr. Long |  | 1 | Nos. | 100 |  |  | Excess(+) | 40 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | 11 kv Disc Insulator T&C Type 45 KN |  | 1 | Nos. | 100 |  |  | Excess(+) | 39 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | 11 kv Disc Fitting |  | 1 | Nos. | 100 |  |  | Excess(+) | 54 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | ABC 3x120+1x95+1x16sqmm |  | 1 | Mtr | 100 |  |  | Excess(+) | 6290 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | PCC Pole 8.5 mtr. Long |  | 1 | Nos. | 100 |  |  | Excess(+) | 51 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | ACSR Dog Conductor |  | 1 | Mtr | 100 |  |  | Excess(+) | 5480 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | SUPPLY OF FOLLOWING MATERIAL BY THE CONTRACTOR FROM THE PVVNL APPROVED VENDORS AS PER GTP APPROVED. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | G.I.Channel 100x50x6x2240mm (9.56kg/mt) with 2 Nos. G.I.Clamp of 65x8mm for Dropper for fuse set & double pole for 11KV line |  | 1 | Nos. | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | G.I.Top Channel 125x65x6mm, 2240 mm long (13.10kg/mt) with G.I. clamp of 75x10mm size, bolts, nuts and washers for 11KV line double pole/ Four Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | G.I.Top Channel 125x65x6mm, 1300 mm long (13.10kg/mt) with G.I. clamp of 75x10mm size, bolts, nuts and washers for 11KV line double pole/ Four Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | 11KV DO Fuse Set (3 Phase) AS PER SPECIFICATION. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | LT PVC CABLE ALU. 3.5X400SQMM |  | 1 | Mtr. | 100 |  |  | Excess(+) | 930 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | LT PVC CABLE ALU. 1X400SQMM |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1580 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | ALU. LEG LONG BAREL OFFICE SIZE (LS) |  | 1 | Nos. | 100 |  |  | Excess(+) | 144 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | THREE PHASE DISTRIBUTION BOX AS PER GTP. |  | 1 | Nos. | 100 |  |  | Excess(+) | 76 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | LT ACB 800 Amp. with Structure (As per Specification) |  | 1 | Nos. | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | G.I.MS Channel 100X50 mm long (13.10kg/mt) with G.I. clamp of 75x10mm size, bolts, nuts and washers for 11KV line double pole/ Four Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 150 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Stay set complete (G.I.Stay rod 16x1800mm, Stay wire 5Kg, Guy insulator, G.I.Stay clamp, bolt, nut & wasther with concrete grouting) for 11KV line as per specification |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | Supply of 11 KV 200 Amp. TPMO (Air Break Heavy Duty Switches) with 02 Nos. 75mm X 40mm X 2800mm galvanised mounting channels as per attached specifications. |  | 1 | Nos. | 100 |  |  | Excess(+) | 11 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Supply and Errection of the Following material for completing the work as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Installation and Commissioning of 11/0.4 KV, 400 KVA T/F Mounted on Plinth/ Chair as per site requirement and providing & fixing of Lugs & copper L-piece (04 No.) of size 400x50x6mm and making of L.T.Connections with complete work in all respects. |  | 1 | Nos | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) ST - 11 Mtr. Long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, Stone Pad Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as an fabrication work if required. Single Pole (a) 11 Mtr. Long ST Pole and PCC 8.5 Mtr Long Pole. |  | 1 | Nos. | 100 |  |  | Excess(+) | 65 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per RESPO. Work includes back filling and proper ramming. Single Pole and Double Pole (a) 11M Long STP and 8.5 Mtr Long PCC Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 91 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | Installation and Fixing of 11 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure of the T/F. The work includes fabrication for proper fixing, if required. Complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | Laying, Sagging and Re-Sagging of AB Cable 3x120sqmm at different locations of T/F as per site requirement. as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 6290 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | Laying Fixing of LT PVC Alu. Cable 3.5x400sqmm at different locations of T/F as per site requirement. as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 930 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | Laying Fixing of LT PVC Alu. Cable 1x400sqmm at different locations of T/F as per site requirement. as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1580 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
33 | Water level earthing by Boring and lowering of G.I. pipe size 40 mm dia & thickness 3mm into the ground at 20 Mtr depth or upto the water level with the lower end of solid copper cone Approx 225 mm long and 750 gm in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the G.I. earth Strip for Transformer neutral connection, the G.I.Earth strip size 50x6mm will be welded to the G.I. pipe and neutral earthing support & other installed equipment in switchyard. All required material provided / supply by the contractor own his cost. |  | 1 | Job | 100 |  |  | Excess(+) | 14 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Construction of New Plinth for 250KVA & above capacity Distribution Transformers, The size of plinth shall be 2M long 2m wide and the height of the plinth shall be 1.50 M with 20 cm. thick top slab with 02 no. 125x65mm MS channel 2 M long embedded in it. The repairing work includes excavation of earth, laying of brick ballast pad for foundation brickwork, CC and plastering and proper curing. The ratio of cement/course sand/fine sand/brick ballast/stone grit as per RESPO schedule including unloading and Loading of the transformer with complete work in all respect. (All work and material in the scope of the Contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
35 | Construction of New Fencing of Transformer. The fencing shall be frame of size 1.5mt x1.80 mt fabricated out of MS angle iron of size 40x40x5 mm having 2 Nos. legs of 45 Cm. long in each frameduly welded and fixed with wire mesh of size 75mm 25mm, 10 SWG within the frame, pressed under MS flat of size 25x5 mm inside the angle iron on all four sides with the help of approx. 20 Nos. bolts and nuts. of 10 mm dia along with cross bracing of 25x5 mm MS flat on every frame will be grouted in 1:2:4 cement mortar with cement, coarse sand 20 mm gauge stone ballast in the size 0.22x0.22x0.45 Mtrs. Every frame after repairing will be painted with one coat of red oxide and two coats of blue synthetic enamel paint of approved make after proper cleaning. The above mentioned frame will be jointed with each other with 70 mm long MS flat of size 25x5mm by first class welding as per site. Fabrication and providing of wire mesh fencing frame for gate of size 1.5x180 Mtrs. Fabricated as items no. 2 and fixing of gate frame at each S/S as per site requirement with grouted frame providing 3 Nos. 100 mm size heavy duty hinges duly welded and having suitable locking arrangment and proper painting. |  | 1 | Job | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
36 | Mounting and installation of above 11 KV 200 Amp. TPMO (Air Break Heavy Duty Switches) with 02 Nos. 75mm X 40mm X 2800mm galvanised mounting channels complete with providing and fixing of required galvanised holding clamps, heavy duty GI pipe 25mm dia with operating handle mechanism, nuts & bolts with supporting channel etc. by the contractor complete in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 11 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
37 | Installation of 800Amp. LT ACB panel with Structure at Transformers as per site requirement with chemical earthing and making of Plinth of the ACB and complete work in all respect as per specification. |  | 1 | Job | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
38 | FIXING OF PIN INSULATOR WITH PIN AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 99 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
39 | FIXING OF DISC. INSULATOR WITH FITTING AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 54 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
40 | Laying, spreading, lifting and final sagging of 3 OR 4 phases ACSR Dog conductor in accordance with Line chart includidng binding and fixing of all accessories in 03Nos OR 04 Nos. Conductor in parallel as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 5480 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
41 | Providing and Fixing of Best Quality Clamp for Lt with Bolts and Nut as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 326 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
42 | FIXING OF MS DROPPER CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
43 | FIXING OF TOP CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
44 | FIXING OF T-OFF CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
45 | FIXING OF Alu. Leg Long Barrel off Size AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 144 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
46 | Instllation and Fixing of Three Phase Junction Box as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 76 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
47 | FIXING OF MS CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 150 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
48 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 11KV and Stay Clamps. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
49 | Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. |  | 1 | Job | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
50 | Providing and fixing of Stone Pad 300x300x75mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
51 | Providing and fixing of Danger Board with Clamp and Nut & Bolt as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 13 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
52 | Providing and Driving of MS earth rod of size 20x2500 mm in earth and jointing through G.I. wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts for pole earthing. Supply Erection, fixing, grouting of stay rod in cement, sand and brick ballast in ration 1:4:8 in Block 600*600*300 mm with binding & nuzzling including providing & fixing of stay insulator complete in all respect with grouting. (All Work and Material in the scope of Contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 40 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
53 | Providing and fixing of Hodling Clamp with Nut & Bolt and Washers for LT ABC and T-off as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 100 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
54 | Providing and fixing of Al. Crimping Lug 1x400sqmm as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 112 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information