## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : fo¦qr forj.k [k.M & prqFkZ] nknjh ds vUrxZr vfrHkkfjr fofHkUu {kerk ds forj.k ifjorZdksa dh {kerko`f) djus gsrq dqy 56 ua0 ifjorZdksa dh LFkkiuk ,oa vU; lEcfU/kr dk;ZA
Contract No: SHORT TERM E-TENDER NO 49/EUDC-II NOIDA/2023-24
G.S.T. AND ALL TAXES INCLUSIVE IN ALL QUOATED RATES.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) The rate quoted by the tenderer shall be inclusive of all duties, taxes (except GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. GST AND ALL TAXES INCLUSIVE IN QUOTED RATES. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder INCLUSIVE OF ALL TAXES AND GST Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with All Taxes and GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Installation of New Distribution Transformer against overloaded transformers in Inreasing Capacity head under EDD-DADRI. (DETAIL OF WORK MENTIONED IN TENDER FORM) | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe carriage of following stock material, from any of the Store Center of PVVNL to work site including Loading from Store and safe unloading at site for Item No. 3 to 7 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | NEW 11/0.4 KV250 KVA T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | NEW 11/0.4 KV 400 KVA T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | ACSR Weasel Conductor |  | 1 | Mtr. | 100 |  |  | Excess(+) | 540 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | LT XLPE Cable 1X400 Sqmm |  | 1 | Mtr. | 100 |  |  | Excess(+) | 320 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | LT AB Cable 3X120 Sqmm |  | 1 | Mtr. | 100 |  |  | Excess(+) | 12163 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | SUPPLY OF FOLLOWING MATERIAL BY THE CONTRACTOR FROM THE PVVNL APPROVED VENDORS AS PER GTP APPROVED. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | G.I.Channel 100x50x6x2240mm (9.56kg/mt) with 2 Nos. G.I.Clamp of 65x8mm for Dropper for fuse set & pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 45 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | 11KV DO Fuse Set (3 Phase) AS PER GTP. |  | 1 | Nos. | 100 |  |  | Excess(+) | 32 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | G.I.Top Channel 100x50x6x2240 mm long (9.56kg/mt) with 2 Nos. G.I.Clamp of 65x8mm for pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 19 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | LT PVC Al. Cable 1x400Sq.mm |  | 1 | Mtr | 100 |  |  | Excess(+) | 1920 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | THREE PHASE JUNCTION BOX with CLAMP AS PER PVVNL APPROVED GTP. |  | 1 | Nos. | 100 |  |  | Excess(+) | 169 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Supply and Errection of the Following material for completing the work as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Installation and Commissioning of 11/0.4 KV, 250 KVA T/F on Plinth/Double Pole/as per site requirement and providing & fixing of Lugs & copper L-piece (04 No.) of size 400x50x6mm and making of L.T.Connections with complete work in all respects. |  | 1 | Nos | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Installation and Commissioning of 11/0.4 KV, 400 KVA T/F on Plinth/Double Pole/as per site requirement and providing & fixing of Lugs & copper L-piece (04 No.) of size 400x50x6mm and making of L.T.Connections with complete work in all respects. |  | 1 | Nos | 100 |  |  | Excess(+) | 28 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | Installation and Fixing of 11 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure of the T/F. The work includes fabrication for proper fixing, if required. Complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 32 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Laying, Sagging and Re-Sagging of LT AB Cable 3x120sqmm at different locations of T/F as per site requirement. as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 12163 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Laying, Sagging and Re-Sagging of LT XLPE 1x400sqmm at different locations of T/F as per site requirement. as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 320 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Fixing of 11 KV Dropper Channel as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 45 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | Fixing of 11 KV Top Channel as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 19 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | FIXING OF PVC CABLE 1X400SQMM at different sites of T/F AS PER SITE REQUIREMENT. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1920 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | Chemical Earthing of T/F : Providing of earth elctrode strip in pipe terminal type chemical earthing proper hot deep galvanization dia 50 mm length 3 mtr down conductor size - 32mm x 6mm terminal connection hole dia 8mm The cavity between the strip & pipes is filled with condutive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be zinc coated the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of Pgs backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested to connect the above chemical earthing with the GI strip of size 32 mm x 6 mm suitable for distribution transformer. |  | 1 | Job | 100 |  |  | Excess(+) | 57 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Water level earthing by Boring and lowering of G.I. pipe size 40 mm dia & thickness 3mm into the ground at 20 Mtr depth or upto the water level with the lower end of solid copper cone Approx 225 mm long and 750 gm in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the G.I. earth Strip for Transformer neutral connection, the G.I.Earth strip size 50x6mm will be welded to the G.I. pipe and neutral earthing support & other installed equipment in switchyard. All required material provided / supply by the contractor own his cost. |  | 1 | Job | 100 |  |  | Excess(+) | 16 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Construction of New Plinth for 250KVA & above capacity Distribution Transformers, The size of plinth shall be 2M long 2m wide and the height of the plinth shall be 1.50 M with 20 cm. thick top slab with 02 no. 125x65mm MS channel 2 M long embedded in it. The repairing work includes excavation of earth, laying of brick ballast pad for foundation brickwork, CC and plastering and proper curing. The ratio of cement/course sand/fine sand/brick ballast/stone grit as per RESPO schedule including unloading and Loading of the transformer with complete work in all respect. (All work and material in the scope of the Contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 30 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | Construction of New Fencing of Transformer. The fencing shall be frame of size 1.5mt x1.80 mt fabricated out of MS angle iron of size 40x40x5 mm having 2 Nos. legs of 45 Cm. long in each frameduly welded and fixed with wire mesh of size 75mm 25mm, 10 SWG within the frame, pressed under MS flat of size 25x5 mm inside the angle iron on all four sides with the help of approx. 20 Nos. bolts and nuts. of 10 mm dia along with cross bracing of 25x5 mm MS flat on every frame will be grouted in 1:2:4 cement mortar with cement, coarse sand 20 mm gauge stone ballast in the size 0.22x0.22x0.45 Mtrs. Every frame after repairing will be painted with one coat of red oxide and two coats of blue synthetic enamel paint of approved make after proper cleaning. The above mentioned frame will be jointed with each other with 70 mm long MS flat of size 25x5mm by first class welding as per site. Fabrication and providing of wire mesh fencing frame for gate of size 1.5x180 Mtrs. Fabricated as items no. 2 and fixing of gate frame at each S/S as per site requirement with grouted frame providing 3 Nos. 100 mm size heavy duty hinges duly welded and having suitable locking arrangment and proper painting. |  | 1 | Job | 100 |  |  | Excess(+) | 30 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Dismentaling of old & used 28 Nos. 100KVA T/F and 28 Nos. 250KVA T/F from the site and safe carriage of its from Site to any Store/Workshop of PVVNL including loading and unloading both ends. |  | 1 | Job | 100 |  |  | Excess(+) | 56 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Providing and Fixing of Best Quality Alu.Lug 400sqmm as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 204 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | Providing and Fixing of Best Quality Alu. Bus Bar as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 89 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | Providing and Fixing of Best Quality Suspension Clamp with Hook as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 401 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | Providing and Fixing of Best Quality Pearcing Clamp as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1247 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | Providing and Fixing of Best Quality MS Holding Clamp as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 608 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
33 | Providing and Fixing of Best Quality MS Nut Bolts and washers as per site requirement. |  | 1 | Kg. | 100 |  |  | Excess(+) | 228 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Fixing and Installation of New Junction Box at Poles with proper connection of LT/HT consumers complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 169 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
35 | Providing and Fixing of Best Quality Dead End Clamps with Nut & Bolts as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information