## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR INCREASING CAPACITY OF POWER TRANSFORMERS AT 33/11KV SUB-STATION-UPEDA (2X5+1X10MVA TO 1X5+2X10MVA), BUSINESS PLAN-2022-23 (SUMMER PLAN 2022-23) IN THE AREA OF EDD-GARH, UNDER EDC., HAPUR.
Tender No: 03(W)/EDCH/2022-23
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | FOR INCREASING CAPACITY OF POWER TRANSFORMERS AT 33/11KV SUB-STATION-UPEDA (2X5+1X10MVA TO 1X5+2X10MVA), BUSINESS PLAN-2022-23 (SUMMER PLAN 2022-23) IN THE AREA OF EDD-GARH, UNDER EDC., HAPUR. | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | cutting the earthing strips and neutral point of 05MVA old T/F at above 33/11KV Sub-Stations. | BI01010001010000000000000515BI0100001113 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Removal of 11KV XLPE Cable connections from 05MVA old T/F at above 33/11KV Sub-Stations. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | Removal of Jumpering of HV/LV side of 05MVA old T/F at above 33/11KV Sub-Stations. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Dragging/Shifting of old 05MVA T/F at above 33/11KV Sub-Stations with the help of Crane and Manual labour and lowering towards ground level tuning the T/F and putting out side of switchyard. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.05 | Opening & removed of Radiators-10Nos. And Conservator Tank-1No. From 10MVA New transformer at 33/11KV S/S./Store. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.06 | Draining out the transformer oil from the Radiators & Tank in 15Empty Drums by Pump in T/F. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.07 | Carriage of 10 MVA Transformers in Trailler, ECS, Hapur/Ghaziabad/Sahibabad/ Meerut/Bulandshahr to site of work, with loading & unloading by crane at both ends, including opening required parts of T/Fs., for carriaging. | BI01010001010000000000000515BI0100001115 | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.08 | Dragging/Shifting of New 10 MVA T/F, Radiators-10 Nos. and Conservator Tank-1 No. & Oil Drumps from dump site to inside switchyard with all accessories on foundation at above 33/11KV Sub-Stations with the help of Crane and Manual labour. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.09 | Mounting/Fixing of all accessories i.e. Radiators-10 Nos. Conservator Tank-01No. And other accessories on T/F tank and tightening of all nut & Bolts of 10 MVA T/Fs. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.1 | Filling of Transformer Oil in the Radiators of 10 MVA T/F with help of Pumping Set. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Connecting the earthing strips at different places and neutral point of the T/F with proper cutting, jointing and welding at site as per requirment and specification given in construction manual issued by RESPO Lucknow. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Making and filling of 11KV Cable Jointing Kit 3x300Sqmm, suitable for 11XLPE Cable as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Laying of 11KV XLPE Cable 3x300sqmm, (Double Circuit) as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 140 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Making the connection of 11KV XLPE Cable with 10MVA T/F including the cost of required Lugs & PVC Tape etc. at 33/11KV S/Ss. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Connecting all jumpers on HV/LV side and 11KV cable with providing cotton tap & empire Tape etc. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Earthing of neutral & body of T/F By Boring and lowering of G.I. Pipe size 32 mm dia… into the ground up to water level 120 fit. With the lower end of solid copper cone approx. 225mm long and 750 gm. in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the M.S. earth strip for T/F neutral connection, the earth strip will be welded to the G.I. pipe and neutral earthing support. | BI01010001010000000000000515BI0100001115 | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | Removal of old & used 11KV XLPE cable 3x185Sqmm and bundling of the same. |  | 70 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | Carriage of old & used 11KV XLPE cable 3x185sqmm, from 33/11KV Sub-Station-Upeda to Electricity Store Centre, Hapur with loading & unloading by crane at both ends. |  | 70 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | Carriage of 05MVA Power Transformers in Trailler from 33/11KV Sub-Station-Upeda to Electricity Store Centre, Hapur with loading & unloading by crane at both ends. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information