## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: S.E. EDC SAMBHAL
Name of Work: fo¦qr forj.k [k.M] lEHky ds vUrxZr Jh lehj vxzoky iq= Jh vuUr dqekj] fuoklh eqjknkckn jksM] lkbZV&”kgtknh ljk; esa fLFkr IykV ij gksdj xqtj jgh 11 ds0oh0 rFkk Jhefr vkjk/kuk vxzoky iRuh Jh lanhi vxzoky] fuoklh ekSgYyk dksVZ iwohZ lkbZV&ekSgYyk vkye ljk; esa fLFkr IykV ij gksdj xqtj jgh 33 ds0oh0 ykbZu dks iw.kZ tek ;kstuk ds vUrxZr f”k¶V djus dk dk;ZA
Contract No: 39/2023-24/EDC SAMBHAL
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE Without Taxes In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT Without Taxes In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Work Detail of 33 KV Hatim Sarai Overhead Line Passing of Smt Aradhna Agarwal W/o Sri Sandeep Agarwal Moh. Kot Poorvi Plot Site Alam Sarai & 11 KV Overhead line SDM Court Feeder & 11 KV Rural Feeder North Emenating from 33/11 KV Sub-Station Sambhal Passing of Sri Sameer Agarwal S/o Anant Kumar Agarwal, Ram Vihar Coloney Site Alam Sarai Shiv Coloney, Sambhal | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2 | Safe carriage of the following material from Store Centre JE's store to work site including loading and unloading at both ends.
2.01 | 13 Mtr./11 Mtr./9 Mtr./8.5 Mtr. Long PCC/ST Poles. |  | 11 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.02 | ACSR Weasel/Dog/Rabbit Conductor. |  | 291 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.03 | 11 KV Aluminum cable of size 3x300 sq.mm. |  | 240 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.04 | Line material such as 33 KV Cross-Arms Chennel, Stone Pad, G.I. wire, Stay Set Complete, Top Chennel, Disc Fitting, Disc Insulator, 33 & 11 KV Pin insulator, F-Breaket etc. |  | 2.3 | MT |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3 | For 33 KV Line, Single support 13/11/9/8.5 Mtr. long ST/PCC Poles Excavation of foundation pit in size of 75x45 cm. having depth of 1/6th of the full length of the support (pole), providing and laying of stone pad (300x300x75mm.) in the bottom of the pit. Erection of support (pole) complete with fixing all other accessories by providing nuts & bolts etc. as per RESPO Norms. |  | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4 | Construction of Tri-Pole Structure on ST Poles including fabrication of MS Angle Channel, Cross Bracing etc. with proving and fitting of all type of clamps made of MS Flat of size 65x8mm. with Nuts, Bolts & washer, grouting of pole in size of 220x45x45 cm. with Cement, Sand and Brick Ballast in the ratio of 1:4:8, as per RESPO Norms. |  | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5 | 11 KV Line, Double Pole structure with 13/11/9/8.5 Mtr. long ST/PCC Poles Excavation of foundation pit in size of 75x45 cm. having depth of 1/6th of the full length of the support (pole). Erection of support (pole) complete work by fixing of D.P. Clamps and all other accessories. as per RESPO Norms. |  | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6 | Grouting of Poles Single line support, Double Poles, Tri pole Grouting of support in CC 1:4:6 (cement, sand and 40 mm. brick ballast) Grouting will be done in the block of size 45cm x 45cm x 1/6th of full length of the support upto ground level as per RESPO Norms. |  | 11 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7 | Grouting of stay rods (20x1800mm.) including all works of excavation, cement concrete in size of (0.60x0.60x0.30)M in the ratio of 1:4:6 (cement, sand and 40 mm. brick ballast) including back filling of soil and proper ramming etc. |  | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8 | Fixing, tightening and nozelling of stay wire with stay rod and stay insulators with the pole of required tension by providing stay clamps, nuts, bolts etc. |  | 16 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9 | Earthing of support with MS Earth Rod of (20x2500)mm. long including excavation of pit and driving MS Rod 3.0 M apart from support and 0.5M below the ground level and connecting below the earth electrodes with the help of G.I. Wire No.6 SWG tightening with nuts and bolts. |  | 11 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10 | Laying 33 KV ACSR Dog Conductor, sagging, stringing and binding with all other accessories on pole as per RESPO Norms. |  | 291 | Mtr |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11 | Construction of 11 KV Underground Line :-
11.01 | Digging of tunch for making hole of under ground 11 KV line. |  | 120 | mtr |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.02 | Providing G.I. Pipe 6” dia for inserting 11 KV Aluminum cable for safety of cable on Single/Double Pole by providing and fixing of MS Clamp, Nuts and Bolts. |  | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.03 | Laying of Under Ground 11 KV Aluminum Cable Size 3 x 300 Sq.mm , sagging, stringing and binding of with all other accessories on pole as per RESPO Norms. |  | 240 | mtr |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.04 | Laying of Cable on STP Pole and Mounting of Cable Jointing Kit (08 Nos) Including Connection both side. |  | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.05 | Making of All Connection and Continue supply |  | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12 | Carriage of following from work site to Store Centre including loading and unloading at both ends :-
13 | Uprooting of 13 Mtr./11 Mtr./9 Mtr./8.5 Mtr. Long PCC/ST/Rail/Gader Poles stacking at a safe place, including loading and unloading at both ends
13.01 | Rail Pole (01 No). Cut Size |  | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
13.02 | Gader Pole (02 No.) Cut Size |  | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14 | Removing of 33/11 KV ACSR Dog/Weasel conductor from all phases on line, making bundle and stacking at a safe place, including loading and unloading at both ends |  | 107 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information