## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR FEEDER BYFURCATION OF LINE/REPLACMENT OF ABC/WIRE, PLINTH, FENCINGH IN CATEGARY-B&C. (14NOS. WORKS) AND OTHER ASSOCIATED WORKS, IN ADDITIONAL BUSINESS PLAN, IN THE AREA OF EDD-II HAPUR, UNDER EDC., HAPUR (uksV%&fuxe eq[;ky; ds dk;kZy; Kki la[;k&1966 fnukad 29-08-2023 esa fufgr funsZ'kkuqlkj ikoj ifjorZd] forj.k ifjorZd] 33 ds0oh0 ,oa 11 ds0oh0 oh0lh0ch0] dUVªksy iSuy] 33 ds0oh0 lh0Vh0@ih0Vh0] ,0lh0,l0vkj0 d.MDVj ¼MkWx@ohty@jSfcV½] fofHkUu lkbZt dh ,y0Vh0 ,0ch0 dsfcy] 33ds0oh0 o 11ds0oh0 ,Dl0,y0ih0bZ0 dsfcy] ,y0Vh0 ,Dl0,y0ih0bZ0 dsfcy] ,l0Vh0 iksy] ih0lh0lh0 iksy] 33 ,oa 11 ds0oh0 fiu bUlqysVj rFkk 33dsoh@11dsoh fMLd bUlqysVj e; fQfVax fMLdkWe Lrj ij Ø; dj miyC/k djk;k tk;sxkA fufofnr dk;Z iw.kZ djus gsrq blds vfrfjDr vU; lHkh vko';d lkexzh fufonknkrk }kjk Lo;a miyC/k djk;h tk;sxhA)
Tender No: 75(W)/EDCH/2023-24
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | FOR FEEDER BYFURCATION OF LINE/REPLACMENT OF ABC/ WIRE, PLINTH, FENCINGH IN CATEGARY-B&C. (14NOS. WORKS) AND OTHER ASSOCIATED WORKS, IN ADDITIONAL BUSINESS PLAN, IN THE AREA OF EDD-II HAPUR, UNDER EDC., HAPUR. | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Carriage of line material (Like: channel, Angle, conductor etc.) from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001113 | 21.12 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Carriage of PCC Pole 8.5 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 41 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 23 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Carriage of new 11KV outgoing VCB. Crompton Greves make, from Electricity store center, Hapur to 33/11KV Sub-Station with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Carriage of new 11KV outgoing Pannel VCB. 11KV CTR 400/200/5Amp., from Electricity store center, Hapur to 33/11KV Sub-Station with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Erection & Fixing of PCC Pole 8.5 mtr. long in 11 KV/LT line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, Cross Arm holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 41 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | Erection & Fixing of ST Pole 11 mtr. long in 11 KV /LT line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, Cross Arm holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 23 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.08 | Laying of ABC Cable (3x95+1x70+1x16) Sqmm., and completion of work properly as per RESPO/Norms, including providing of required material like clamps, nuts bolts etc. | BI01010001010000000000000515BI0100001115 | 300 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | Laying of ABC Cable (3x50+1x35+1x16) Sqmm., and completion of work properly as per RESPO/Norms, including providing of required material like clamps, nuts bolts etc. | BI01010001010000000000000515BI0100001115 | 500 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.1 | Laying of Trenchless 11 KV XLPE 3x185Sqmm Cable undergound (30x2=60 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms., including providing of required material. | BI01010001010000000000000515BI0100001115 | 60 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Laying of Trenchless 11 KV XLPE 3x240Sqmm Cable undergound (155x2=310 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms., including providing of required material. | BI01010001010000000000000515BI0100001115 | 310 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Laying of Trenchless 11 KV XLPE 3x70Sqmm Cable undergound (270x2=540 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms., including providing of required material. | BI01010001010000000000000515BI0100001115 | 540 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Making and filling of 11KV Cable Jointing Kit 3x185Sqmm,, outdoor type, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of jointing kit, lugs and tape etc., as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Making and filling of 11KV Cable Jointing Kit 3x240Sqmm,, outdoor type, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of jointing kit, lugs and tape etc., as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 8 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Making and filling of 11KV Cable Jointing Kit 3x70Sqmm,, outdoor type, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of jointing kit, lugs and tape etc., as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Laying, Stringing and final sagging of ACSR Dog Conductor after binding from Insulator, as per RESPO/Drawing Norms. | BI01010001010000000000000515BI0100001115 | 12420 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | Laying, Stringing and final sagging of ACSR Weasel Conductor after binding from Insulator, as per RESPO/Drawing Norms. |  | 65878 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | Grouting of ST/PCC supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials. |  | 23 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops. (including cost of stay set complete.) |  | 6 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | Earthing of supports with MS earth Rod of (20x2500)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts.(including cost of earth Rod complete.) |  | 3 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | Fabrication, erection and fixing of V-Type 11KV X-Arm angle 65x65x6mm as per RESPO Drawing/Norms by providing required clamps, nuts and bolts. |  | 58 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | Removal of all connections & other associated works of old & jarjar VCBs's for dismantling/Removal of the same. |  | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | Removal of old & jarjar 11KV outgoing VCB, from existing place in control room and shifting the same outside the control room at 33/11KV Sub-Stations. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | Carefully & safely shifting of 11KV outgoing VCB Crompton make and Ougoing pannel VCB 11KV CTR/400/200/5Amps, from outside to inside the switchgear room at the place of removed VCB's and erection/Installation of 11KV VCB's after fixing of anchor GI nuts & bolts of proper size for completion of work by providing required material, as per RESPO/Drawing Norms. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | Connecting, Jumpering & other associated works of installed new VCBs's including cost of required material like tape etc., as per RESPO/Drawing Norms. |  | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.26 | Providing and installation of Battery Set (24 V, 150AH) and completion work properly as per RESPO Drawing/Norms, including providing required all materials. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.27 | Providing and installation of Battery Charger (24 V) and completion work properly as per RESPO Drawing/Norms, including providing required all materials. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.28 | Providing of stay wire 7/10 SWG for completion of proper work as per RESPO Norms. |  | 30 | Kgs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.29 | Providing of G.I. wire 4 MM/ 6/8/10 SWG for completion of proper work as per RESPO Norms. |  | 150 | Kgs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.3 | Removal of old & damaged (scrap) 8344Kgs. conductor and bundling of the same |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.31 | Removal of old & damaged ST Pole and opening of all accessories. |  | 8 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.32 | Carriage of old and damaged STP from Site of work to JE Store/ESC Hapur with loading and unloading at both ends. |  | 8 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.33 | Carriage of old and damaged VCB from Site of work to JE Store/ESC Hapur with loading and unloading at both ends. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.34 | Carriage of old and damaged coductor-8344Kgs, from Site of work to JE Store/ESC Hapur with loading and unloading at both ends. |  | 83.44 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.35 | Jumpering work properly as per RESPO/Norms. |  | 28 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information