Eligibility Criteria/Pre-Qualifying Requirements

# QUALIFICATION OF TENDERES -

  - The tenderers shall either themselves be manufacturers of the equipment offered or accredited representatives of such manufacturers in India or of their principals aboard with whom they may be having collaboration. Such accreditation should be at least of one year on date of tender.

  - Relevant documents in support of the above must be furnished along with undertaking of the manufacturers and a certificate that they are participating in the tender individually but in case of award, the employer should give preference in award to the manufacturer of the material/equipment. If these documents are not furnished along with the tender bids, the offer will be liable to be rejected summarily.

  - The bidder should have provided the Facility Management services for HES driven pre-paid metering to at least 25,000 No. of Energy Metering nodes. Work order and completion certificates needs to be submitted by the bidder.

The bidder has to give the live demonstration of successful running of such projects to the technical evaluation committee of PVVNL & based on the report of technical committee & above requirement, the bidder shall be considered as technically qualified.

  - Minimum Average Annual Turnover of Rs. 60 Crore for best three years out of last five financial years. However, for UP based industries average turnover of Rs 30 Crore per year will be acceptable.

  - Net worth of the bidder should be positive. Net worth means the sum total of the paid up capital and free reserves (excluding reserves created out of revaluation) reduced by aggregate value of accumulated loses (including debit balance in profit and loss account for current year) and intangible assets.

  - Solvency: - The bidder should have a minimum solvency of Rs. 10 Crore or credit facility for the same from Nationalized/scheduled bank.

  - The bidder must possess bureau of Indian Standard Certification (ISI Mark) and valid ISO 9001:2008 certification for meter manufacturing, ISO 27001:2005 for information security management system and ISO: 14001- 2004 for environmental management system. Relevant license and certificates to be enclosed.

  - The bidder shall submit a copy of valid certificate of capability maturity model integration (CMMI) of minimum level 3 issued by recognized body like SEI etc. along with his bid. Relevant license and certificates to be enclosed.

  - Relevant documents in support of the above must be furnished along with bid. If these documents are not furnished along with the tenders, the price bid of the firm may not be opened, the offer will be liable to be rejected summarily.

The bidder should have successfully completed the turnkey/semi- turnkey work of the following nature in the last three financial year as prime contractor from the date of opening of bid part-1: -

- Should have successfully erected and commissioned similar or higher rating work in a single turnkey/semi turnkey order, having minimum order value of 80% of the estimated cost of the present tender specification, or

- Should have successfully erected and commissioned similar or higher rating work in maximum two turnkey/semi turnkey order, having minimum order value of 50% each of the estimated cost of the present tender specification, or

- Should have successfully erected and commissioned similar or higher rating work in maximum three turnkey/semi turnkey order, having minimum order value of 40% each of the estimated cost of the present tender specification.

  - No trial Order shall be given.

  - Bidders will submit proof of legal entity like company, LLP, authorized to do business under applicable acts e.g. The Companies act 1956, with due registrations with tax authorities / departments of central and state governments. Copies of such documents (PAN, GST etc.) shall be mandatory to submit as part of bid submission documents

  - The bidder should provide detailed information on any litigation or arbitration arising out of contracts completed or under execution by it over the last five years. A consistent history of awards involving litigation against the Bidder may result in rejection of Bid

# OPERATIONAL EXPERIENCES:

Offered equipment should have given three years proven trouble free operational service in tropical climate. However, in case of equipment being manufactured in India under valid FOREIGN COLLABORATION, operating experience in tropical climate of offered collaborator’s equipment shall also be acceptable provided copy of valid collaboration agreement for the equipment offered is submitted with the tender. Further, in case of offer of imported equipment, the three(3) years operating experience will be considered in respect of those areas only which are similar to the tropical condition prevailing in India.

# Testing Facilities:

Service Provider /Meter Manufacturer must have NABL accredited lab at their works for carrying out such routine and acceptance tests, type test as prescribed in the relevant ISS. Documentary evidence of existence of such facilities shall be submitted along with the bid, failing which price may not be opened.

# Type Test:

# For indigenous bids or fully imported bids:

The offered equipment must have been fully type tested as per relevant ISS and/or any other specified international standards during the last 5-year period to be reckoned from the date of opening of tender. Photocopy of such type test reports/certificates must be submitted along with tender bid. The type test certificates of prototype manufactured and tested by foreign collaborators of the tenderer at their works shall not be acceptable for indigenously manufactured equipment.

# For indigenous bids under valid foreign collaboration.

  - The offered indigenously manufactured or collaborators manufactured equipment should have been type tested and report submitted with the tender.

  - The collaborator's equipment shall have three years operating experience under tropical climate.

# The bidder shall furnish details of meters with specification, supplied by them in Govt./Power sector utilities, during the previous five years along with copy of orders received purchaser of similar quantity & rate of failure of supplied meters. They have to submit an undertaking regarding this along with the bid.

# Final Testing of meters:

- Testing of meters will be done at CPRI Lab only.

- On offer of meter inspection by the meter manufacturing firm an inspection team of minimum two officers conversant with meter from the Discom will be formed which will select the meter samples randomly from the meters offered for inspection as per clause no H2.1 of Annexure H of IS.

- Inspection team will seal the sample meter in their presence and will clearly note down the meter & seal number in their sealing certificate. Inspection team will get the sealed meter samples enclosed in packing in such a way that there is no way of tempering the samples in their presence. Inspection team will mention on their sealing certificate serial number of each seal with their specimen signature, and this will be mentioned in inspection report.

- Meter manufacturer will be fully responsible for payment of all expenditure involved in delivery of the sealed and packed meter samples to CPRI lab by Inspection team, bringing back and all kind of testing charges.

- CPRI lab will test all the Acceptance Test on sample meters as per IS 13779 (With all latest amendments) in which following process is mentioned-

H-1 LOT

H- 1.1 In any consignment, all the meters of the same type and rating manufactured by the same factory during the same period shall be grouped together to constitute a lot.

H- 1.2 Sample shall be tested from each lot for ascertaining the conformity of the meters to the requirements of specified acceptance test.

H-2 SCALE OF SAMPLING

H- 2.1 The number of meters to be selected from the lot depends upon the size of the lot and shall be in accordance with Table 26.

| Table 26 Sampling Plan |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Lot Size | N 1 1 | N 2 2 | (N1+N2) | C1 | C2 |
| 1 | 2 | 3 | 4 | 5 | 6 |
| Up to 300 | 8 | - | 8 | 0 | - |
| 301 to 500 | 13 | 13 | 26 | 0 | 2 |
| 501 to 1000 | 20 | 20 | 40 | 0 | 3 |
| 1001 and above | 32 | 32 | 64 | 1 | 4 |
| 1) Size of the first sample. |  |  |  |  |  |
| 2) Size of the second sample. |  |  |  |  |  |

H-2.2 The meters shall be taken at random from the lot. The procedure given in IS 4905 may be adapted.

H- 3 NUMBER OF TESTS AND CRITERIA FOR ACCEPTANCE

H- 3.1 Test of No-Load Condition and Starting Condition

A sample of N1 meters selected according to col 2 of Table 26 shall be tested for the above tests. Any meter failing in any one of these tests shall be considered defective. If the number of defectives found in the sample is less than or equal to C1 the lot shall be considered to be conforming to these tests. If the number of defectives is greater than or equal to C2, the lot shall be considered as not conforming to these tests. If the number of defectives is between C1 and C2, a further sample of N2 meters shall be taken according to col 3 of Table 26 and subjected to these tests. If the number of defectives in two samples combined is less than C2, the lot shall be considered as conforming to these tests, otherwise rejected.

H1- 3.2 (i) Tests of insulation resistance, (ii) AC voltage tests, (iii) Test of power consumption, (iv) test of meter constant/registration. (v) limits of error and interpretation of test results and adjustment (if required).

From the sample of meters which have been drawn according to H-3.1 and those that have passed all tests of H-3.1. A sample of 8 meters shall be tested, all of which shall pass for conformity to these tests. If any of the meters fails in any of these tests, the whole lot shall be declared not conforming to the requirements of these tests.

H- 3.3 Tests for Repeatability of Error

Above tests shall be carried out on 3 samples selected from above 8 meters under H-3.2 and shall be tested for repeatability of error tests separately. If any one of the meters fails, the whole lot shall be declared not conforming to the requirements of these tests.

H- 3.4 The lot shall be considered as conforming to this specification, if provisions of H-3.1, H-3.2 and H-3.3 are satisfied.

6.1	All tests other than which are not performed by the CPRI lab will be performed by Inspection team of Discom as per approved GTP/standard technical specification for dual source dual register 2 way communicable meters issued by UPPCL/DISCOM at the meter manufacturer works.

6.2 	Till the successful completion of type test at CPRI Lab, service provider will neither use the meters for installation on consumer premises nor any payment will be done against this supplied lot of meters. In case of getting CPRI Test lab report not as per standards then meter supplying firm has to take back all the meters of that lot on its expenditure.

6.3 	If during inspection by Inspection Team or Type Test performed by CPRI are not found conforming to technical specification or relevant IS following penalty will be imposed on the service provider-

| Case | Failure | Penal Action |  |  |
| --- | --- | --- | --- | --- |
|  |  | Replacement | Financial Penalty | Debarment from business/ Blacklisting |
| Failure-1 | 1st time failure in fresh lot | 100% | NIL | NIL |
| Failure-2 | 2nd time failure in subsequent lot or replaced previous lots of same PO | 100% | 10% of the ex-works (including F&I) value of the lot plus GST. | NIL |
| Failure-3 | 3rd time failure in subsequent lot or replaced previous lots of the same PO | Not Allowed | NIL | Debarment/ blacklisting of meter manufacturer from business in All DISCOMs for 1 year (+) |

# DATE OF CONSIDERATION:

The above cited experience and manufactured quantities shall be counted as on the date of opening of the tender. All statements and claims should be duly supported by authenticated copies of documents without which the tender is liable to be rejected summarily.