## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR VARIOUS ELECTRICITY LINE WORKS, IN DEPOSIT SCHEME (RUNNING CONTRACT), IN THE JURISDICTION OF EDSD-PILAKHWA/ANWARPUR OF EDD-II, HAPUR, UNDER EDC., HAPUR.
Tender No: 122(W)/EDCH/2023-24
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | FOR VARIOUS ELECTRICITY LINE WORKS, IN DEPOSIT SCHEME (RUNNING CONTRACT), IN THE JURISDICTION OF EDSD-PILAKHWA AND ANWARPUR (UBARPUR) OF EDD-II, HAPUR, UNDER EDC., HAPUR. | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Carriage of line material (like LT ABC, 11KV XLPE Cable, ABC and 11KV Cable Jointing Kit indoor/outdoor type etc.) from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001113 | 42.9 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 90 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | Carriage of PCC Pole 8.5 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 40 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Carriage of 10KVA to 250KVA from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Carriage of 11KV CT/PT Unit from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Carriage of Metering Cubical Set Complete, from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | Erection & Fixing of PCC Pole 8.5 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, Cross Arm holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.08 | Erection & Fixing of PCC Pole 8.5 mtr. long in LT. line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing L.T. Pin Clamps, M.S. Flat of size 50x6 & Schacle Insulator of size 75x90mm, with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | Erection & Fixing of STP Pole 11 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, Cross Arm holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.1 | Fabrication, erection and fixing of double pole on ST Pole 11 mtr. long with fixing of M.S. Top & Dropper Channel, M.S. S/S Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting as per RESPO Drawing/Norms by providing top and dropper clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 40 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Fabrication, erection and fixing of double pole on PCC Pole 8.5 mtr. long with fixing of M.S. Top & Dropper Channel, M.S. S/S Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting as per RESPO Drawing/Norms by providing top and dropper clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Mounting, Placing and connecting from LT/HT side of 11KV, 10 to 250KVA T/F as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Mounting, Placing and connecting from LT/HT side of 11KV, CT/PT Units as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Laying of 140/160mm O/D PN-4PE-80 PN-4 grade UV stabilized HDPE pipe as per IS of 6meter, for laying of underground Cable as per RESPO/Norms, including cost of above HDPE pipe. | BI01010001010000000000000515BI0100001115 | 200 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Laying of 11 KV and 33KV XLPE Cable undergound (50x2=100 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 200 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Road restoration charge for pucca road crossing as per RESPO/Drawing Norms. | BI01010001010000000000000515BI0100001115 | 100 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | Road restoration charge for foothpath side as per RESPO/Drawing Norms. | BI01010001010000000000000515BI0100001115 | 100 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | Laying of 11KV ABC of various capacity and completion work properly, as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 100 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | Laying of 11KV XLPE Cable 3x35-3x70+3x120-3x185sqmm and completion work properly, as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 450 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | Laying of LT ABC of various capacity and completion work properly, as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 100 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | Erection & Fixing of Distribution Box on pole by provding 02 Nos. D/B Clamps & proper size nut & bolts. | BI01010001010000000000000515BI0100001115 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | Providing and fixing of Suspension Clamp with Eye Hook as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | Providing and fixing of Dead End Clamp with Eye Hook, as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | Making and filling of 11KV Cable Jointing Kit, Indoor/outdoor type, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of lugs and tape etc., as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | Installation of 11KV Metering Cubical Complete work as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.26 | Fabrication & Fixing of T-Channel on pole by providing Holding Clamps, F-Clamps & Proper size nuts & bolts, as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 12 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.27 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops. | BI01010001010000000000000515BI0100001115 | 40 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.28 | Earthing of supports with MS earth Rod of (20x2500)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts. |  | 40 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.29 | Grouting of ST/PCC supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials. |  | 130 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.3 | Wrapping of barbed wire on 11KV ST/PCC poles as anti-climbing device for a length of 0.9mtrs. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a hieght of 2.75 mtr from the ground complete, including providing & fixing of lower end & upper end clamps made of M.S. Flat 40X5mm complete with nuts & bolts and all other required material and T&P. |  | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.31 | Fabrication of Guarding Angle X Arm & other requisites material for guarding by drawing 02Nos G.I Wire and making loop at suitable distance as per RESPO drawing/Norms by providing holding clamps, 02Nos. Eye bolts made of M.S. round size 12mm dia-100mm long & Cross Arm clamps made of M.S. Flat of size 50X6mm and bolts as per norms of RESPO Lucknow . |  | 50 | mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.32 | Laying , Stringing and final sagging of ACSR Weasel Conductor after binding from Insulator, as per RESPO/Drawing Norms. |  | 1000 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.33 | Laying , Stringing and final sagging of ACSR Rabbit Conductor after binding from Insulator, as per RESPO/Drawing Norms. |  | 200 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.34 | Laying , Stringing and final sagging of ACSR Dog Conductor after binding from Insulator, as per RESPO/Drawing Norms. |  | 300 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.35 | Providing & Fixing of G.I. pipe 6"dia Class-B over 11KV 3X70 and 3x120Sq.mm XLPE cable before mounting the cable at double pole. The work includes fitting of clamps, sealing of top and bottom of pipe and one end of pipe is to be burried under earth about 500mm earch including mounting and clamping the cable on double pole structure and making connection with overhead line at both ends. |  | 50 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.36 | Construction of T/F plinth suitable for 250KVA T/F (size of 2 x 2 x 1.5 mt.) as per drawing, cc work in foundation in ratio 1:4:8 (Cement, Sand & Brick ballast). Ist class brick work in side walls cc ratio of 1:4 (cement & fine sand). 12mm thick plaster in ratio 1:4 (cement & fine sand). The RCC work on top of plinth in ratio 1:2:4 after duly filling of brick ballast inside the plinth & ramming the same, including cost of all material & labour. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.37 | Erection & Fixing of 11KV. Fuse set on ST Pole 11mtr long, by providing all required materials, including cost of 11KV Fuse set. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.38 | Erection & Fixing of 11KV. TPMO set on ST Pole 11mtr long, by providing all required materials, including cost of 11KV TPMO Set. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.39 | Providing fixing and fabrication of fencing (MS 5mp 5x6mm fencing, 6 feet hight including civil welt 2x4x3) around the T/F plinth upto 6 fit height on top of T/F plinth, including cost of all material and labour as per RESPO/drawing/Norms. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.4 | Providing & Fixing of Danger Board, including fixing of all accessories by providing all required materials (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.41 | Providing & Fixing of Number Plate alongwith all required accessories (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms. |  | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.42 | Dismantling & Removal of old existing STP/PCC pole after digging of pit and opening of all accessories. |  | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.43 | Removal of old & used ACSR Conductor and opening form insulator and bundling of the same. |  | 780 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.44 | Dismantling & Removal of old & used 10/25/63/100KVA T/F and opening of all accessories. |  | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.45 | Carriage of old & used STP/PCC from site of work to Electricity store center, Hapur with loading and unloading at both ends on Kachha Packka road. |  | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.46 | Carriage of old & used ACSR Conductor from site of work to Electricity store center, Hapur with loading and unloading at both ends on Kachha Packka road. |  | 10 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.47 | Carriage of old & used 25/63KVA T/F from site of work to Electricity store center, Hapur with loading and unloading at both ends on Kachha Packka road. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.48 | Earthing of neutral & body of T/F By Boring and lowering of G.I. Pipe size 32 mm dia… into the ground up to water level 120 fit. With the lower end of solid copper cone approx. 225mm long and 750 gm. in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the M.S. earth strip for T/F neutral connection, the earth strip will be welded to the G.I. pipe and neutral earthing support. |  | 6 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.49 | Providing & Fixing Chemical earthing of Transformers Equipment the ground surface where it will be bolted to the M.S. earth strip for connection the earth strip will be welded to the earthing and neutral support, as per RESPO/Norms. |  | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.5 | Jumpering work properly as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 50 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information