## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST VERY SHORT TERM E-TENDER NO. 36/EUDC-I/2023-24/NOIDA (WORKS) FOR CARRYING OUT THE WORK REPLACEMENT OF DAMAGED, JARJAR & NON REPAIRABLE LT FEEDER PILLER FOR DUPLAEX SEC 135 NEAR HD-278, HD-79, HD-266 TO HD-273 FEEDED FROM FEEDER NO.-02, 33/11 KV S/S SECTOR-135, NOIDA IN AREA OF EUDSD-VIII, NOIDA UNDER EUDD-V, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA.
Contact No: 0120-2970431
The bidder quoted rate should be inclusive GST & all other taxes)
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. The bidder quoted rate should be inclusive GST & all other taxes. 2. Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC. 3. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder with GST & all other taxes Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 5 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 6 | 54 | 7
1 | REPLACEMENT OF DAMAGED, JARJAR & NON REPAIRABLE LT FEEDER PILLER (BRANCH DISTRIBUTION PANNEL) OF SIZE 4x2.5x2 FEET WITH PROVIDING FOR DUPLAEX SEC 135 NEAR HD-278, HD-79, HD-266 TO HD-273 FEEDED FROM FEEDER NO.-02, 33/11 KV S/S SECTOR-135, NOIDA IN AREA OF EUDSD-VIII, NOIDA AS PER FOLLOWING :- | BI01010001010000000000000515BI0100001128 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Supply of new L.T. Feeder Pillar (Branch Distribution Pannel) as per following specification with all relevant certificate :- 1) LT Feeder Pillar Box (Branch Distribution Pannel) shall be of 14 SWG HR sheet, having (2) doors, 1 in front and 1 doors on back side of 14 SWG HR sheet. Doors should have proper locking arrangements with providing crome locks of standard make. It should have a canopy on top in order to prevent it from water ingress in rains. The doors of box should be welded with robust quality hinges and PVC GaskEt with provision of 3 hinges on each door and handle on each door with PVC Gasket. The periphery of door of the LT Feeder Pillar Box (Branch Distribution Pannel) shall be provided with lining of rubber/ PVC to prevent entry of rain, insects, lizards, rats etc. so as to make it vermin proof. 2) The dimension of Feeder Pillar Box (Branch Distribution Pannel) 4(Height) X 2.5(Width) X 2(Depth) Feet (With Canopy). 3) 04 Nos. Bus Bar insulation coated fo size 1000x75x10mm. made of aluminum for red, yellow, blue & neutral phases suitable for 400 Amp. 4) 01 No. MCCB of 250 Amp. of L&T / Havell’s / ABB make for disconnecting of Supply. 5) 18 Nos. KIT KAT Fuse of 415V, 150 Amp. each capacity tested as per IS shall be provided with 6 Nos. on each phase so as to cater to 6 Nos. 3 Phase connections of conusmer. 6) Aluminum crimping lugs of size 400 / 240 / 120 / 95 / 70Sq.mm. and proper size thimbles shall be provided for safe termination of incomer as well as individual service cable as per qty. requirement. 7) Bakelite sheet shall be provided on the base of channel meant for mounting the Kit Kats. 8) All nuts, bolts & washers used shall be electro galvanized. 9) The height of erected feeder pillar box (Branch Distribution Pannel) approx. 2 feet from the earth on powder coating base of angle iron size 40x40x5mm frame with 04 nos. legs of 3 feet each (1 feet grout of angle on earth bottam, 1.6 feet grout in plinth and 6 inch gap in pannel base and plinth) 10) Grouting & Plinth of Feeder Pillar Box (Branch Distribution Pannel) as per site requirement complete in all respects. 11) The panel case consisting of door and roof (canopy) shall be powder coated with chemical process (weather proof) of Off-white color (Or as per direction) both inside and outside. Before painting, the sun faces shall be thoroughly cleaned from dust, grease and rust. Ientification no. shall be written as per direction. 12) Sundry item. | BI01010001010000000000000515BI0100001129 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | Disconncetion of all Consumer connection from pannel as per requirement. | BI01010001010000000000000515BI0100001130 | 14 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | Reconncetion of all Consumer connection from pannel after replacement as per requirement. | BI01010001010000000000000515BI0100001131 | 14 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.04 | Dismantling of damaged L.T. Feeder Pillar (Branch Distribution Pannel) from earth on work site. | BI01010001010000000000000515BI0100001132 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.05 | Carriage of above dismantled Pannel from works site to JE store / central store & proper stacking with loading & unloading. | BI01010001010000000000000515BI0100001133 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Installation of above new L.T. Feeder Pillar (Branch Distribution Pannel) in place of damaged L.T. Feeder Pillar (Branch Distribution Pannel) with grouting, plinth and required items complete in all respect. | BI01010001010000000000000515BI0100001134 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.07 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR ABOVE NEW L.T. FEEDER PILLAR (BRANCH DISTRIBUTION PANNEL) (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) :- | BI01010001010000000000000515BI0100001135 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.08 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 50 mm length 3 mtr - 32mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for above new L.T. Feeder Pillar (Branch Distribution Pannel). | BI01010001010000000000000515BI0100001136 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.09 | Providing and fixing of GI strip of size 32 mm x 6 mm suitable for above new L.T. Feeder Pillar (Branch Distribution Pannel) | BI01010001010000000000000515BI0100001137 | 42 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.1 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. | BI01010001010000000000000515BI0100001138 | 42 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.11 | Providing & fixing of Aluminium Crimping Lug of size 240 Sq.mm. | BI01010001010000000000000515BI0100001139 | 150 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.12 | Cartage of Earthing complete etc. from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. | BI01010001010000000000000515BI0100001140 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.13 | Excavation of earth and driving of M.S. earthing rod of size 20x2500 mm in earth and jointing through G.I wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts etc. as per RESPO schedule Complete in all respects. | BI01010001010000000000000515BI0100001141 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.14 | Cartage of LT XLPE Cable 3.5x240 Sq.mm. from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. | BI01010001010000000000000515BI0100001142 | 350 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.15 | Drilling of dia 160 mm in single bore by trench less method by horizontal boring machine at a depth of 1.5 mtrs below the ground level complete in all respects. | BI01010001010000000000000515BI0100001143 | 310 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.16 | Providing of 06 Mtr long pieces of HDPE pipe 6 Inch Dia PN 4 PE 63 (PVVNL approved) after inspection of competent committee at manufacturing site of the items with actual guarantee period. | BI01010001010000000000000515BI0100001144 | 310 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.17 | Laying and interconnecting of above 06 Mtr long pieces of HDPE pipe 6 inch Dia PN 4 PE 63 (PVVNL approved). | BI01010001010000000000000515BI0100001145 | 310 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.18 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop. | BI01010001010000000000000515BI0100001146 | 2 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.19 | Providing of HDPE Socket suitable for HDPE pipe 6 inch dia. | BI01010001010000000000000515BI0100001147 | 52 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.2 | Fixing of above HDPE Socket LT XLPE Cable 3.5x240 Sq.mm. and 6 inch dia pipe. | BI01010001010000000000000515BI0100001148 | 52 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.21 | Road Restoration charges for hot mixed pakka road / CC road/ mix soil/ normal soil/ soft & hard rack as it is when start of work as per authority norms. | BI01010001010000000000000515BI0100001149 | 2 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.22 | Laying and pulling of LT XLPE Cable 3.5x240 Sq.mm. through HDPE pipe and at Double Pole / in loop / riser. | BI01010001010000000000000515BI0100001150 | 350 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.23 | Hi port test for LT XLPE Cable 3.5x240 Sq.mm. | BI01010001010000000000000515BI0100001151 | 350 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.24 | Providing & Fixing of Stone Route Marker with proper marking. | BI01010001010000000000000515BI0100001152 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information