## PVVNL-MT/COM/11(s)/22-23

TECHNICAL SPECIFICATION FOR 33 KV PILFER PROOF  METERING CUBICLES

- GENERAL:

This specification covers the design, manufacturing, testing and supply of 33 KV indoor type metering cubicle made of M.S. sheet

  - The metering cubicle shall be totally enclosed, dust and vermin proof having four separate compartments as below,

“one for incoming cable, one for outgoing cable ,one for mounting CT’s & PT’s and one for electronic meter as per enclosed drawing.”

  - The metering cubicle shall be supplied with three nos. 33KV single phase CT's three nos. 33KV single phase PT’s with connecting strips, support for 33KV cable, CT's and P.T. with necessary clamping arrangement, Bus Bar etc.

  - All the equipments shall comply with the requirements of the relevant I.S. specifications.

  - List of raw material to be used along with name of suppliers should be submitted with the tender.

1.5	The complete metering cubicle shall be guaranteed for a period of 42 months from the date of receipt of material at site or 36 month from the date of commissioning which ever is earlier. During the guarantee period bidder shall be responsible for free replacement at site for any defect/damage reported by the purchaser. The defective/damaged equipment should be replaced with in five days of intimation of damage by the purchaser, failing which a penalty of Rs. 200 per day shall be imposed on the firm for the delayed period.

- CONSTRUCTION:

2.1	The 33KV-metering cubicle shall be fabricated with M.S. sheet having thickness not less than 2.0mm and 2.5mm for separation walls between compartments. The overall dimensions of the cubicle shall be approximately 1800mm (Height) x 2100mm (Width) x 1550mm (Depth). These dimensions may vary  as per design of the manufacturer taking into care the minimum clearances of 370mm in case of PT’s and 320 mm in case of CT’s, between two phases as well as between phase to earth and subject to the condition that complete metering cubicle passes  impulse test as per clause 5.3.3 of  technical specification. Tentative drawing of 33 KV metering cubicle has been attached as annexure I .

2.2	All the edges and joints shall be made and welded in such a way so that no access inside the cubicle shall be possible through them and shall thus provide strength to robust mechanical construction both for transportation and installation for its use.

2.3	The metering cubicle shall be totally enclosed and shall be provided with one no. hinged doors each for lower (CT/PT) & upper (L.T) compartment. All the doors shall be made of M.S. sheet of thickness not less than 2.0 mm and shall rest on the collars along the four sides of the cubicle so that the doors remain flushed with the body of the cubicle. The two no. side compartments for incoming & outgoing cables shall be provided with hinged double door arrangement.

2.3.1	The hinges of the doors shall be concealed type (welded from inside) so as to eliminate any chance of de-hinging without causing any damage to the cubicle.

    - All the doors shall be provided with synthetic / semi – synthetic gasket to make it dust & vermin proof.

    - Each door shall be provided with a handle, locking arrangement and two no. sealing arrangements.

2.4	The metering cubicle shall rest upon two Nos. M.S. Channel support of approximate size 100 mm x 50 mm x 5 mm welded at bottom along its depth.

    - Each of these supporting channels shall have suitable arrangement for foundation bolts at two places there by making hole of 12mm dia for the foundation bolts, which shall be tightened by means of nuts provided inside the cubicle.

    - The metering cubicle shall be provided with G.I. Earthing strip of size 50 mm x 5 mm welded at the two opposite base angles provided with welded bolt of 6mm dia welded form inside the cubicle. The earthing strip can be connected by tightening a bolt form outside the metering cubicle at two opposite ends.

2.5	The surface of the metering cubic shall be cleared suitably and made smooth and shall be provided with two coats of grey colour epoxy paint on the outside and two coats of white colour epoxy paint in the inside the cubicle as well as that of doors.

2.6	The metering cubicle shall have four separate compartments, separated by M.S. sheet of 2.5mm thickness as given below.

    - .0     UPPER (LT) COMPARTMENT:

The upper compartment of the metering cubicle shall be called L.T. compartment and shall have approximate minimum height of 450 mm.

The compartment shall house a trivector meter and also a check energy meter (both not in scope of supply) along with its associated wiring.

2.6.1.1	For fixing of KWH Trivector meter and check energy meter in this compartment two Nos. slotted channel of 25mm X 25mm X 2mm size shall be welded vertically at their two opposite ends and similarly two Nos. slotted channel of the same size shall be placed horizontally, so that horizontal channel can be bolted at desired heights for installing the meter inside the cubicle.

2.6.1.2	There shall be one toughened glass (fixed with araldite), (Approx, size 300 x 200 mm) window protected by wire mesh (approx. square 25mm) over it, on the door of the upper compartment. The glass shall be fitted within channel from inside of window.

The height of Glass shall be such that it is convenient to take meter reading at or below eye level.

The window shall be provided with a proper sealing arrangement.

2.6.1.3	The L.T. Compartment shall essentially contain the following:

Hanger of slotted Channels for mounting main meter (L&T, Secure, Datapro, Duke make etc.) and check meter for having flexibility for mounting of meter vertically and horizontally, (Meter not in scope of this supply).

2.6.1.4	The terminal end of MRI cord connecting Electronic TVM optical port should be fixed on main cover of meter chamber with a sealable sheet cover of size 40 mm x 75 mm. Proper sealing arrangement for this cover shall also be made.

2.6.1.5     The doors shall be provided with one no. locking and 2 no. sealing arrangement.

2.6.2.0	LOWER (CT/PT) COMPARTMENT:

The lower compartment of metering cubicle shall be called CT/PT compartment and shall have approximate dimensions 1250mm (height)X 800mm(width)X 1550mm (depth). Both the side walls of these compartments will made of M.S sheet of thickness not less than 2.5mm.

2.6.2.1	This compartment shall house 3 Nos. 33 KV single phase CT, for R, Y & B phases and 3 No. 33 KV single Phase PT’s, copper connecting strips between 33 KV CT's, PT’s & Bus bar.

2.6.2.2	The compartment shall be provided with one no. hinged door, which shall rest on the collar of the M.C. such that it becomes complete dust-proof & vermin proof. The door shall be provided with a separate one No. locking and two nos. sealing arrangements so that inside access is not possible when sealed. Suitable provision shall also be made at three places for welding of  the door with the cubicle by providing M.S. Flat of size 2cm X 6cm on door and cubicle each.

The CT/PT Compartment shall essentially contain the following:

- 33 KV Current Transformer (single Phase) 	:	3 Nos.

for R, Y & B Phases:

- 33 KV / 110 V Potential Transformer (1 Phase)	:	3 No.

√3          √3

- 'Cu' Bus bar (sufficient length)to connect CTs.

(CT Terminals)(for incoming outgoing cable 40.00 mmx5.00mm)	:1 Set

- Flexible copper flat strip of 20X3.5 mm 0.5 mm or 8 SWG:	1 Set

Copper wire to connect the CT/Bus bar and P.T.

(f) L.T. wiring for the secondary of the PT and 	:	1 Set

CT circuits.

(g) Suitable provision of silicagel to absorb moisture inside the cubicle should be 		 made.

2.6.2.3	Two No. Side (cable) Compartments: There shall be two no. side compartments for incoming and outgoing cables. These compartments shall be mounted on side walls of main (CT/PT) compartment. The dimensions of these compartments will 1100mmX650mmX1550mm.These compartments will have a clearance of 150mm from ground level so as to facilitate easy entry & exit of 33KV cables. These compartments shall have cable termination and suitable clamping arrangement for 33KV XLPE Cable (incoming or outgoing). Provision of suitable space and arrangement of proper orientation of cable termination shall be made so that there is no problem in fixing the incoming or outgoing cable. These compartments shall be suitably joined electrically from incoming & outgoing sides of CTs of Main (CT/PT) chamber through suitable size copper rods duly insulated from walls of the cubicle. These compartments shall be welded on the main compartment. These copper rods will be threaded on cable side so as to facilitate jointing of cable termination lugs by suitable nuts (nuts one also to be provided with rod).

Each cable compartment shall be provided with 1 no. cable entry at the bottom, of the size suitable for 33KV XLPE cable of 3X120 sq mm along with suitable metallic cable glands .

Door of each compartments shall be provided with 1 no. locking arrangement & 2 no. sealing arrangement.

2.6.2.4	CT's & PT's shall be rigidly mounted on the frame.

  - A plate of suitable size shall be provided on the outside of the cubicle which shall have the following information to be engraved on the plate:

PASCHIMANCHAL VIDYUT VITRAN NIGAM LIMITED

Name of the consumer	:

Service Connection No.	:

Sanctioned Load	:

Date of release of connection	:

Type of load cont./Non cont.	:

Meter No. & make	:

Line CTR/PTR& Sl. No.	:

Meter CTR/PTR	:

Class of accuracy of CTs	:

Class of accuracy of PT	:

CT/PT MF	:

Dial factor for energy/for demand	:

Overall MF for energy / for demand:

Date of last checking

In addition to the above, CT ratios and their class of accuracy shall be painted / 	engraved on the front side of the panel by the supplier. The CT ratio, Sl. no. & its 	manufacturers name shall also be embossed on each CT. The information 	regarding the suitability of the Cubicles for loads shall also be indicated by paint / 	engraving in bold letters.

2.7	Apart from other informations, following information shall essentially be 	provided on 	name plate of 33 KV metering cubicles.

(i) Name of Manufacturer (ii) Month/Year of Manufacture (iii) Guarantee Period 	42 Months.

2.8    The firm should have eligibility type test of the offered equipment as elaborated in the relevant clause of PQR, as per relevant ISS and/or any other specified international standards during the last 5-year period issued from ERDA/NTHM/ CPRI. Photocopy of such type test reports/ certificates must be submitted along with tender bid. The type test certificates of prototype manufactured and tested by foreign collaborators of the tenderer at their works shall not be acceptable for indigenously manufactured equipment.

  - If the firms do have the eligibility type test as per Sl. No. 2.11  above but do not have valid type test report as per current technical specification with revised parameters as prescribed by PVVNL for cross sectional area of conductor, core, current density, shall have to give undertaking to submit valid type test report of offered equipment issued by

CPRI/ERDA only within maximum period of three months time. Keeping in view of the timely completion of projects supplies shall be accepted with the provision that 50% payment shall only be released and the balance 50% may be released only after submission of valid type test report.

3.0	ELECTRICAL COMPONENTS:

The supplier shall be original manufacturer of the epoxy resin cast CT/PT or accredited representative of such manufacturer. The bidder must have facility to cast epoxy resin by hot casting process under vacuum for CTs and PTs at his own works. These CT & PT should have been type tested as per relevant ISS (latest revision) in a Govt. accredited National Test House such as CPRI, Bangalore / Bhopal etc. during the last five years from the date of Tender opening. A brief detail of the various components to be provided in the metering cubicle is give below:-

3.1	CURRENT TRANSFORMERS:

There shall be three nos. Single Core single ratio dry type epoxy resin cast current Transformers as per IS: 2705: 1992 of latest revisions thereof as per details mentioned below:-

TYPE: Dry type epoxy Resin cast CTs.

Capacity		10/1A,15/1A,20/1A,25/1A,30/1A,40/1A, 50/1A,60/1A,70/1A, 75/1A, 100/1A, 200/1A

(a)	Rated Voltage		33KV

(b)	No. of cores		One

(c) 	Rated VA Output	`	2.5 VA

(d)	Rated continuous Thermal		As per IS: 2705: 1992

Current temperature rises over ambient.

(e)	One minute withstand Power		As per ISS

frequency voltage (for primary

and secondary)

Class of accuracy		0.5  S.

(f) Current density at rated current(Max)	    1.5 Amp. Per sq. mm

(g) Current density at STC for 1 second(max)	    165 Amp. Per sq. mm

(h) Cross sectional area of primary as per current   Should be as per  rated current density    density			      or as per current density at STC			     (for 1 second) whichever is higher.

Short time thermal current rating	   			  10/1 to 20/1-7.8KA for 0.5 sec

25/1 to 40/1-7.8 KA for 1.0 sec

50/1 to 250/1-13.0 KA for 1.0 sec

| (j). | Rated dynamic current rating |  | 2.5 times of short time thermal current rating |
| --- | --- | --- | --- |
| (k) | Rated continuous thermal current |  | 1.2 times of rated primary current |
| (l). | Instrument Security factor |  | < 5 |
| (m). | All other characteristics and test parameter |  | As per IS: 2705/1992 (latest version) |
| (n). | Max temperature rise over ambient temp of 50º at rated continuous thermal current at rated frequency rated bush. |  | 45ºc |

Material

(i)	Core	High-grade non-ageing electrical low

loss core of superior CRGO silicon

sheet steel.

(ii)	Conductor	Super enameled copper wire

(iii)	Insulation	Resin cast.

(iv)	Base 	MS Hot dip galvanized.

Secondary Termination	From and effective Termination S 1& S2

shall be clearly marked.

Fault Level	13.1. KA for 1 Sec

The current transformer should have been type tested and routine tested as per IS: 2705/1992 or latest amendment thereof.

3.2         POTENTIAL TRANSFORMER:

There shall be three Nos. single phase, potential Transformers (one per phase). The primary and secondary winding of 33 KV PT should be wound on insulating craft paper. These will be dry type Epoxy resign cast, air cooled conforming to IS: 3156/1992 or latest amendment thereof. Entire PT assembly i.e. core and coil should be encapsulated under vacuum impregnation in epoxy resin. The PTs shall have a ratio of 33 / √3 KV / 110 / √3 V and with a rated burden of 25 VA and of accuracy class 0.5. The material of primary and secondary winding should be copper. The cross sectional area of primary should be 0.015 sq. mm(Minimum) and that of secondary winding should be 1.6 sq. mm (Minimum). These will be connected in star-star formation for phase-to-phase voltage ration of 33 KV/110 V. There will be no HT fuses in the primary side and secondary side of the potential Transformer. Rated voltage factor of PT should be as per ISS. Potential transformer should have been type tested as per IS: 3156/1992 or latest version thereof

  - INSULATORS:

The insulators if required for all the bus supports shall be epoxy resin cast, indoor type. The hardware used shall be electroplated M.S. The insulators shall be conforming to relevant ISS.

3.4	PT LINKS:

The bus –bar and HT side of PT shall be connected through a flexible copper strip of size 25mm X 3.5 mm X 0.5 mm or 8 SWG Copper Wire such that HT Terminals of PT are not subjected to any compression or tension forces.

3.5	L.T. WIRES:

The LT wiring shall be done with PVC insulated flexible copper wires of cross wires of cross section not less than 2.5 Sq. mm. of reputed make, conforming to relevant ISS. These will be provided with lugs and ferrules at termination in the LT Compartments, suitable colour, code, PVC insulated flexible Copper (without joints) will be neatly bunched and dressed and without any joints should be used. These wires shall connect secondaries of CTs. and PT. Proper code and numbers should be marked on ferrules for individual CT& PT connections.

3.6	MAKE OF THE COMPONENT:

List of raw material to be used along with names of the suppliers should be submitted 	with Part-I of the tender. Make of various components as detailed above and as being 	given below.

3.7	HARDWARE:

Hot-Dip Galvanized of any standard make.

3.8	PAINT:

Epoxy – Paint of standard make.

3.9      EPOXY RESIN: –

Dr. Beck, Huntsman, Atul.

4.0	INSPECTION AND TESTING:

All Cubicle shall be inspected and tested at manufacturer works to verify that these are being supplied in accordance with relevant standards. Technical Specification, Guaranteed Technical Particulars and acceptance and routine tests.

Inspection of material offered for inspection shall be carried out jointly by the representative of Superintending Engineer (DQC), PVVNL, Meerut.

While offering for inspection / testing confirming to the effect that the cubicle have successfully withstand the routing tests (along with test results)  is required to be submitted for each lot offered for inspection Superintending Engineer (DQC), PVVNL, Meerut.

All inspection used in inspection and testing should be properly calibrated and sealed once a year. Calibration certificate when demanded by the inspecting officer shall be provided / produced for verification purpose. In case of any dispute regarding calibration, instruments shall be sealed and singed by the representative of the supplier and purchaser and will be sent to test house / Govt. Lab / Govt. institution of repute, for calibration at the cost of supplier. The result of such testing shall be binding on the supplier.

Purchaser reserves the right to get the components like CT's / PT's etc. inspected / type tested before dispatch by any independent inspection agency at the cost of purchaser in case the equipment with stand the type test, otherwise the supplier has to bear such cost in addition to any other action deemed appropriate by the purchaser.

One sample of CT of any ratio randomly selected from each offered lot, shall be opened for verifying the diameter & cross sectional area of primary coil conductors including verification of GTP

Testing Facility: - The manufacturer must have testing facilities at their works as per clause No. 1.2.3 of "Instruction to Tenderer" to carry out all the routine & acceptance test (including partial discharge test) as mentioned below. List of Testing equipment with photo copy of calibration certificates should be enclosed with Part- II of the tender. Schematic drawing showing each and every details, dimensions and wiring diagrams shall be submitted necessary for each type of metering cubicle.

4.1	Type test:

All the type tests as listed below shall be carried out for the equipment strictly as described as per the relevant ISS(or latest amendment thereafter).

4.1.1	Current Transformers (As per IS: 2705 / 1992 or its latest Amendment)

(A) Type Testing will be done on CT of any one ratio if-

(i)	The type tested CT has maximum dynamic AT’s in confirmation to IS:2705, 1992 Clause no. 9.6.2 (Notes)

(ii)	The shape size construction of all the ratio is same.

However if shape size & construction varies for different ratio’s then all type test shall be repeated accordingly for each shape, size & construction.

a)	Short-time current test.

b)	High Voltage power frequency on primary windings.

c)	High Voltage power frequency on secondary windings.

d) 	Lightning impulse test

e)	Determination of error according to the requirements of appropriate accuracy class

f)	Temperature rise test on any one selected sample of each ratio.

g)	Partial discharge test

h)	Instruments security factor (ISF) test as per IS:2705. Part-II or any latest amendment.

4.1.2	Potential Transformers: (As per IS: 3159 / 1992 or its latest amendment. Type test on PT shall be done on any one unit

- Determination of error according to the requirements of accuracy class.

- Temperature rise test.

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

- Impulse Voltage Test.

4.1.3	Complete Metering Cubicle

The complete metering cubicle after fitting all CTs and PTs shall be type tested for impulse test by ERDA or CPRI test lab. The type test report shall be submitted by the bidder

4.2.1	Routine Tests: -

The following shall constitute the routine test and acceptance tests.

4.2.2 	Current Transformers

- Verification of terminal markings and polarity

- High Voltage power frequency test on primary windings.

- High voltage power frequency test on secondary windings.

- Over voltage inter turn test.

- Determination of error according to the requirements of appropriate accuracy class.

- Partial discharge test in accordance with IS: 11322 / 1985.

- Instruments security factor test (IFS) as per IS:2705.

4.2.3	Potential Transformers:

- Verification of terminal markings and polarity

- Power frequency dry withstand test on primary windings.

- Power frequency dry withstand test on secondary windings.

- Determination of error according to the requirements of appropriate accuracy class.

- Partial discharge test in accordance with IS: 11322 / 1985

4.3	Acceptance Test:

4.3.1 	Dimensional check of metering cubicle

4.3.2   High voltage power frequency test on primary winding at 70 KV for one minute and secondary winding 3 KV for one minute for metering cubicles.

4.4	Current Transformers

- Verification of terminal markings and polarity

- High Voltage power frequency on primary windings.

- High Voltage power frequency on secondary windings.

- Determination of error according to the requirements of appropriate accuracy class

- Temperature rise test.

- Partial discharge test

- Instruments security factor test (IFS) as per IS:2705.

4.5	Potential Transformers

- Verification of terminal markings and polarity

- High Voltage power dry withstand test on primary windings.

- High voltage power dry withstand test on secondary windings.

- Determination of error according to the requirements of appropriate accuracy class.

- Temperature rise test

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

- Partial discharge test

5.0	In case of any discrepancy between specification and relevant standard, provision 	contained in this specification shall prevail.