## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Executive Engineer, Electricity Construction & Works Division, Ghaziabad | [54 empty] | Bought Out
Name of Work:-Works at proposed (i) Construction of 33/11KV Substation Dankaur Gautambudh Nagar CAPACITY (1X10)MVA (ii) Construction of 33KV line for feeding of 33/11KV Substation Dankaur Gautambudh | [54 empty] | Direct
Tender Reference No : 08/ECWD/Gzb/2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) |  |  | Total Unit Price incl. GST (in Rs.) | [26 empty] | Total Amount excl. GST (in Rs.) | Total Amount incl. GST (in Rs.) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply of following Material (From Sl.No.1 to 62) Disc Insulator Polymeric B&S type 70KN | item1 | 183 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | Disc Fitting B&S type 70 KN | item2 | 183 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | 33 KV Composite Polymer Pin Insulator with Nut and washers | item3 | 651 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | 11 KV Composite Polymer Pin Insulator with Nut and washers | item4 | 18 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | Stay set complete (G.I.Stay rod 20x1800mm, Stay wire 7/8SWG 10Kg, Guy insulator, G.I.Stay clamp, bolt, nut & wasther with concrete grouting) for 33KV line as per specification | item5 | 304 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | Stay set complete (G.I.Stay rod 16x1800mm, Stay wire 5Kg, Guy insulator, G.I.Stay clamp, bolt, nut & wasther with concrete grouting) for 11KV line as per specification | item6 | 8 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | PCC Pole, 9.0 Mtr. Long | item7 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | 11 Mtr long STP (SP-55) (Bottom portion Galvanised) | item8 | 250 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | 13 Mtr. STP (SP-72) (Bottom portion Galvanised) | item9 | 15 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | G.I. Wire 6 SWG | item10 | 3006 | Kg | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | G.I. Wire 8 SWG | item11 | 1000 | Kg | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | G.I. Wire 16 SWG | item12 | 100 | Kg | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | 11KV Lightening Arrestor | item13 | 12 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | 11KV DO Fuse Set (3 Phase) | item14 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | 11KV TPMO complete set (As per Specification) | item15 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | V-Type Cross Arm 100x50x6 mm G.I channel for 33KV line | item16 | 173 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | G.I.Top Channel 125x65x6mm, 3200 mm long (13.10kg/mt) with G.I. clamp of 75x10mm size, bolts, nuts and washers for 33KV line double pole/ Four Pole | item17 | 38 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | G.I. Top Channel 125x65x6 mm, 2240 mm long (13.10kg/mt) with 2 Nos. G.I.Clamp of 65x8mm for S/s Transformer double pole | item18 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | G.I.Top Channel 100x50x6x2240 mm long (9.56kg/mt) with 2 Nos. G.I.Clamp of 65x8mm for 11KV line double pole | item19 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | G.I. Channel 100x50x6 mm, 2400 mm long (9.56kg/mt) with G.I.Clamp of 65x8mm for dropper channel of 33KV line double pole/four pole | item20 | 97 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | G.I.Channel 100x50x6x2028mm (9.56kg/mt) with 2 Nos. G.I.Clamp of 65x8mm for Dropper for fuse set & double pole for 11KV line | item21 | 10 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | G.I Angle Iron 65x65x6mm, (5.80kg/mt) 4300 mm long bracing with 4 Nos. G.I. clamps of 65x6mm, bolts, nuts and washers for 33KV line | item22 | 20 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
23 | G.I Guarding angle 75x75x6 mm, (6.80kg/mt) | item23 | 3500 | Kgs. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
24 | M.S.Round size of 32mm dia for Earth Mat, Delta earthing and Bridge earthing. | item24 | 2500 | Kgs. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
25 | Terminal Gantry Galvanized Structure as per specification | item25 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
26 | 33KV Line Isolator 800 Amp. | item26 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
27 | 33KV Bus Isolator 800 Amp. | item27 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
28 | Galvanized Structure for 33 KV Isolator with Plinth & Foundation as per specification | item28 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
29 | Galvanized Structure 33 KV Single Phase CT (3 Nos.) with Plinth & Foundation with junction box as per specification | item29 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
30 | Galvanized Structure for 33 KV Single PT (3 Nos.) with Plinth & Foundation with junction box as per specification | item30 | 1 | Set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
31 | Galvanized Structure for 33 KV VCB with Plinth & Foundation as per specification | item31 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
32 | 33KV Post Insulator | item32 | 18 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
33 | Galvanized Structure for 33 KV Post Insulator (3 nos.) with Plinth & Foundation as per specification | item33 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
34 | 33 KV Fuse Set | item34 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
35 | Galvanized Structure for 33 KV Fuse set as per specification | item35 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
36 | 33KV Lightning Arrestor with surge counter. | item36 | 6 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
37 | Galvanized Structure for 33 KV Lightning Arrester (3 nos.) with Plinth & Foundation as per specification | item37 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
38 | G.I. Cable support Structure of size 65x65x6mm angle as per specification | item38 | 5 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
39 | G.I. T-type Structure of size 100x50x6mm channel for support of copper bus bar as per specification | item39 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
40 | Power Transformer Neutral G.I. L-Type Stand of size 100x50x6mm channel with copper bound as per specification | item40 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
41 | 90 lbs Rail Pieces for Transformer 44.64 Kg/M | item41 | 7 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
42 | LT PVC Al. Cable 4x16Sq.mm | item42 | 40 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
43 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item43 | 40 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
44 | Heat Shrinkable straight through cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item44 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
45 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 11KV XLPE 3x300 Sq.mm. cable | item45 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
46 | Heat Shrinkable indoor type end termination cable jointing kit suitable for 11KV XLPE 3x300 Sq.mm. cable | item46 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
47 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 11KV XLPE 3x185 Sq.mm. cable | item47 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
48 | Heat Shrinkable indoor type end termination cable jointing kit suitable for 11KV XLPE 3x185 Sq.mm. cable | item48 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
49 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 11KV XLPE 3x50 Sq.mm. cable | item49 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
50 | Heat Shrinkable indoor type end termination cable jointing kit suitable for 11KV XLPE 3x50 Sq.mm. cable | item50 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
51 | 4x2.5 mm Sq. Armoured Control Cable with laying and connection with VCB/CT/PT/Power T/f etc. | item51 | 400 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
52 | 2x2.5 mm Sq. Armoured Control Cable with laying and connection with VCB/CT/PT/Power T/f etc. | item52 | 200 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
53 | 24 Volt Battery and Battery Charger cum Inverter with cabinet complete set | item53 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
54 | T & P of Sub-Station Switchgears as per Specification. | item54 | 1 | set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
55 | Furniture of Substation as per Specification (01 No. Office Chair, 01 office table (size 4x6Ft), 01 No. bench of size 6x1.25 ft., 01 No. rack, 01 No. steel stool & 01 No. Almirah) | item55 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
56 | 1.0 X 2.0 mtr. Size Rubber mat 20 mm. thick | item56 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
57 | 4.5 Kg. CO2 Fire Extinguisher, portable type (As per specification) | item57 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
58 | 5 Kg. Dry chemical powder fire extinguisher, portable type (As per specification) | item58 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
59 | Fire Buckets (6 nos.) with stand, filled with dry sand as per specification | item59 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
60 | 33/11KV S/S Name board (SMC) with stand as per specification | item60 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
61 | 10 inch Exhaust fan complete in all respect | item61 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
62 | ACSR Panther Conductor | item62 | 200 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
63 | Carriage of following material from PVVNL store (From Sl.No.63 to 79) ACSR Dog Conductor | item63 | 24754 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
64 | 11KV/0.433 KV, 3 Phase, 63 KVA Transformer (BEE standard, 3 star rating self protected type), Al. wound | item64 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
65 | 33 KV 1 Ph CT 400/200/1 Amp. | item65 | 6 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
66 | 33KV 1 Ph PT 33KV/110 V | item66 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
67 | 33 KV VCB 1250 Amp. (As per specification of PVVNL) | item67 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
68 | 33KV 3x300 mm2 XLPE Al. Cable | item68 | 3995 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
69 | 11KV 3x300 mm2 XLPE Al. Cable | item69 | 100 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
70 | 11KV 3x185 mm2 XLPE Al. Cable | item70 | 250 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
71 | 11KV 3x50 mm2 XLPE Al. Cable | item71 | 50 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
72 | LT Aluminium XLPE Insulated Armoured Cable of size 3.5x70 sqmm. | item72 | 20 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
73 | LT Aluminium XLPE insulated unarmoured 1x50 Sq. mm. Cable | item73 | 30 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
74 | 33kV Control Panel for Double T/F Control without Differential Relay | item74 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
75 | 33kV Control Panel for Single Feeder without Differential Relay | item75 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
76 | 11KV Incoming CTR 600/300/5A, 350MVA | item76 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
77 | 11KV Outgoing CTR 200/100/5A 350 MVA | item77 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
78 | ACSR Weasel Conductor | item78 | 100 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
79 | Cartage of empty cable drum from site to PVVNL store including loading & unloading at both ends respectively. | item79 | 8 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
80 | Erection of following Material & Miscellaneous Electrical Works. Construction of terminal gantry as per details:- Terminal Gantry: Excavation of earth for making 2 Nos. pits of size (1.4x0.75x2.2)M | item80 | 4.62 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
81 | Fabrication of Terminal Gantry by using 4 Nos. of 8.70 M long (175x85)mm, 19.5 kg/meter or (100x116)mm, 23.1 kg/meter R.S. Joist with bracing of the same by G.I. Angle iron or size (50x50x6) mm & providing & fixing 2 Nos. of 3.2 m long pieces of G.I. Channel of size (125x65x6)mm for Top as well as Dropper channel & Composite Polymeric Pin insulator. The work also includes cutting, drilling and welding with alignment etc. for proper completion of work. | item81 | 12.5 | Qtl | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
82 | C.C. work in ratio of 1:4:8 (cement, fine sand and brick ballast) of size (1.40x0.75x0.15)m for 2 Nos. pits for making bed. Work includes proper ramming etc. | item82 | 0.32 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
83 | C.C. work of ratio 1:3:6 (cement, coarse sand & 20 mm size stone grit) for the structure of 02 Nos. of pre-fabricated legs of terminal gantry (8.2 m long) as per drawing No. RES-38 size of plinth (1.4x0.75x2.7)m. | item83 | 5.67 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
84 | 12mm thick plaster with cement mortar ratio 1:4 (cement & fine sand) of plinth of 0.4 m upper side, | item84 | 5.6 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
85 | Supply & fixing of stone pad | item85 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
86 | Isolator Structure Erection of Isolator structure (Line and Bus) 04 Nos. size of plinth (0.9x0.30x1.0) m as per drawing No. RES-39 Excavation of earth for making 08 Nos. pits of size (0.9x0.30x1.0)m. | item86 | 2.16 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
87 | Fabrication of Isolator structure (Bus & Line) by using 4.0 m long 04 Nos. of G.I. channel of size (125x65x6)mm with bracing by G.I. Angle (40x40x5)mm/ (50x50x6)mm size and providing 02 Nos. top channel of G.I. Angle (75x75x6)mm and 2.6m long on both side of Isolator. The work also includes cutting, drilling, welding and proper alignment of the same for completion of work. | item87 | 15.2 | Qtl | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
88 | C.C. work in ratio of 1:4:8 (cement, fine sand and brick ballast) of size (0.90x0.30x0.15)m for 8 Nos. pits for making bed. Work includes proper ramming etc. | item88 | 0.324 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
89 | C.C. work of ratio 1:3:6 (cement, coarse sand and 25 mm stone grit) for pre-fabricated structure of Line and Bus isolator size of plinth (0.90x0.3x1.5)m for 8 Nos. | item89 | 3.24 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
90 | 12mm thick plaster with cement mortar ratio 1:4 (cement & fine sand) of plinth of 0.4m upper side. | item90 | 9.84 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
91 | Supply & fixing of stone pad. | item91 | 16 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
92 | L.A.’s P.I.’s, C.T’s, Fuse Set and CT/PT (09 No.) structure:- Febrication & Erection of Lightening Arrestors, Post Insulators/Fuse Set, C.T.’s, P.T's structure and Plinth for the same as per drawing No. RES-39 details:- Excavation of earth (0.30x0.30x1.0)m for 18 Nos. Pits of above structures. | item92 | 1.62 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
93 | Fabrication of L.A.’s, P.I.’s, C.T.’s, P.T and Fuse Set structure by using G.I. Channel (125x65x6) mm size and 3.5 m minimum height with 2 Nos. G.I. Angle (50x50x6)mm size on top of structure for installation L.A.’s, P.I.’s & Fuse Set. | item93 | 1260 | Kgs. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
94 | C.C. work in ratio of 1:4:8 (cement, fine sand and brick ballast) of size (0.30×0.30×0.15)m for 18 Nos. pits for making bed for each structure. Work includes proper ramming etc. | item94 | 0.243 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
95 | C.C. work of ratio 1:3:6 (cement, coarse sand and 25 mm size stone grit) for the above plinths for structure of L.A.’s, P.I.’s, C.T.’s & Fuse Set 18 Nos. after ramming of earth of size (0.3x0.3x1.5)m. Over stone pad. | item95 | 2.43 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
96 | 12mm thick plaster with cement mortar ratio 1:4 (cement & fine sand) of plinth of 0.4m upper side. | item96 | 11.67 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
97 | Plinth for 10 MVA Transformer Construction of plinth for 10 MVA, 33/11 KV Transformer of (3.46x3.46x1.0)m (0.50m below ground level and 0.5 m above ground level) as per details & drawing attached (All required matrials provided/Supply by the contractor own his cost):- Excavation of earth (3.7x4.7x0.5)m | item97 | 8.7 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
98 | Flooring of plinth in C.C. 1:4:8 (cement, sand & brick ballast) for making foundation bed. Size (3.7x4.7x0.15)m. | item98 | 2.61 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
99 | 1st Class brick work for side walls size 0.345 m wide upto 0.3m height and 0.23 m wide upto 0.35 m height cm C.C. ratio of 1:4 (cement & fine sand) | item99 | 3.1 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
100 | Filling of brick ballast in plinth in ratio 1:4:8 (cement, coarse sand & brick ballast) with proper ramming. Size (4.0x3.0x0.65)m. | item100 | 7.8 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
101 | R.C.C. work on the top of plinth in ratio 1:2:4 in (4.46x4.46)m size and 0.20m in thickness by using G.I. Tor of 12 mm dia. 12 Nos. in each direction across to each other. The work also includes cutting, bending of G.I. Tor etc. | item101 | 3.09 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
102 | Quantity of M.S. Tor of size 12 mm dia required for reinforcement of plinth in R.C.C. work should be 28 nos. bars of 3.4 mtr length and 22 nos. bars of 4.40 mtr. length. Work also includes cutting, bending and laying etc. in the T/F plinth. | item102 | 200 | Kgs. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
103 | Grouting of 02 Nos. 90/105 lb. Rail pieces of 3.46m long and (50x50x6)mm G.I. Angle in R.C.C. work at the top of plinth work also includes cutting of rail and angles pieces etc. | item103 | 13.84 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
104 | 12mm thick plaster with cement mortar ratio 1:4 (cement & fine sand) of plinth of 0.5m upper side. | item104 | 23.35 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
105 | Plinth for 33 KV V.C.B. Construction of plinth for the structure of 33 KV VCB & C.T.’s as per details for 02 No. (All required materials provided / Supply by the contractor own his cost) :- Excavation of earth of size (2.4x1.5x1.0)m pits for construction of plinth. | item105 | 7.2 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
106 | Brick Ballast ratio (1:4:8) (cement, sand & brick ballast) for foundation work (2.4x1.5x0.15)m plinth. | item106 | 1.08 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
107 | R.C.C. work in ratio 1:2:4 (cement, coarse sand & stone grit) of 20m size for making plinth of size (2.4x1.5x1.0)m and grouting of foundation bolts 04 Nos. for 33 KV VCB. | item107 | 7.2 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
108 | 12mm thick plaster with cement mortar in ratio 1:4 (cement & fine sand) of plinth of 0.4m upper side size (2.4x1.5x0.4)m. | item108 | 13.44 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
109 | Earth Mat Work Excavation of earth of size (0.5x0.75x260)m in switchyard area as per drawing for laying of 32 mm dia M.S. Round and 50x6mm size G.I. strip and refilling & ramming of the same earth into the trenches after completion of work. | item109 | 97.5 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
110 | (i) Laying of 32 mm dia M.S. Round Bar in 0.75m deep trenches as excavated in items. 1(a) | item110 | 260 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
111 | (ii) Welding with lap joint minimum length 150mm over lapping on both side of item 1(b) (i) shall be done so that all the edges may fill completely with high quality Arc welding. All joints shall be painted with black bituminous paint. | item111 | 30 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
112 | Jointing of 32mm dia M.S. Round in earth mat at cross joint using high quality Arc welding 75mm piece of 32 mm dia M.S. Round shall also be welded to make the joints strong for transfer the fault current. Work also included cutting welding and painting with black bituminous paint of joint etc. | item112 | 27 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
113 | Fabrication of 32mm dia for 3.0 m long electrodes and driving them into ground so that the top of M.S. Round/Electrode remains at least 0.75 m below the ground level and jointing of earth electrode with the Earth Mat by using 75mm long piece of M.S.Round using high quality Arc welding and paints of joints with black bituminous paint. | item113 | 30 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
114 | Providing & Laying of G.I. Earth strip of size 50x6mm for connecting the Earth Mat with steel structure & chain link fencing’s posts. The work also includes cutting, bending, traight-tening, over-lapping and welding the Earth Strip with Earth Mat and various steel structures by using high quality Arc welding in already digged trenches. | item114 | 150 | Mt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
115 | Painting of Earth Strip of size (50x6) mm with one coat of ready mixed primer with two coats of ISI mark synthetic channel green paint. | item115 | 110 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
116 | Providing & Erection of Chemical pipe earthing including electrode, chemical with 3mtr. Long, 80mm dia and 3mm thick G.I. Pipe & G.I. strip of 25x3mm must be used for feeder double Pole, Substation T/F, L.A & Substation (All required matrials provided/Supply by the contractor own his cost). | item116 | 7 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
117 | Earthing of L.A's & Transforer neutral : Making of delta with 03 No. 03mtr. 32mm dia M.S. round bar electrode and Fabrication of 32 mm dia bar for 3.0 m long electrodes and digging them into ground so that the top of M.S. Round/Electrode remains at least 0.75m in air and jointing of earth electrode with the delta by using 75mm long piece of M.S. Round using high quality Arc welding and paints of joints with black bituminious paint. | item117 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
118 | Construction of Control cable trench (30Mtr) as per details Excavation of earth in size 0.650x0.40m. | item118 | 7.8 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
119 | C.C. work in foundation in ratio 1:4:8 (cement, sand & brick ballast) with proper ramming in size 0.65x0.15 mtr.) | item119 | 2.93 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
120 | First Class Brick work in cement mortar in ratio 1:4 in size 0.23x0.32 Mtr. | item120 | 2.2 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
121 | 25mm thick C.C. in floor of Cable Trench in ratio 1:2:4 (cement, coarse sand and stone ballast) 20mm gauge in size 0.3 mtr. Width. | item121 | 9 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
122 | Grouting of G.I. Strip of size 450x25x6mm in cable trench 100mm above floor level and at equal space distance 300mm. | item122 | 100 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
123 | Grouting of G.I. Angle Iron of size 50x50x6mm in upper edge of trench. | item123 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
124 | Plastering of Trench in Cement, Mortar in ratio 1:4, 12mm thick in cable trench. | item124 | 40.8 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
125 | Fabrication and fixing cable trench cover of G.I. Angle size 50x50x6mm of size 0.3m wide 0.5 to 1.0 mtr. Length with proper welding of 8 mm size of bar 2 Nos. in length and 6 Nos. in width including cost of CC casting & RCC in Ratio 1:2:4 (cement, coarse sand and stone ballast) (i) 0.5 Mtr. Long | item125 | 10 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
126 | (ii) 1.00 Mtr. Long | item126 | 25 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
127 | Painting of Structures Painting of the following structure with one coat of ready mixed primer and two coats of ISI Mark Aluminium paint after rubbing with sand paper to the surface of the structure including labour and T&P complete in all respect. Double pole. | item127 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
128 | All welding joint of G.I.Steel structure. | item128 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
129 | Installation of 33/11 KV, 10 MVA Transformer Shifting of available 10 MVA, 33/11 KV, Transformer to transformer plinth in Switch Yard. | item129 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
130 | Erection of shifted Transformer at plinth by fixing all accessories like radiators, conservator tank, filling the transformer oil to desired level and ensuring that there is no leakage, complete job in all respect. | item130 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
131 | Water level earthing by Boring and lowering of G.I. pipe size 40 mm dia & thickness 3mm into the ground at 20 Mtr depth or upto the water level with the lower end of solid copper cone Approx 225 mm long and 750 gm in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the G.I. earth Strip for Transformer neutral connection, the G.I.Earth strip size 50x6mm will be welded to the G.I. pipe and neutral earthing support & other installed equipment in switchyard. All required material provided / supply by the contractor own his cost. | item131 | 5 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
132 | Fabrication and erection of neutral earthing L Type support made of G.I. Channel size 100x50mm. Structure shall be 4 Mtr. Long with 1 Mtr. Arms. Structure shall be grouted in ratio 1:3:6 in block size 300x300x700mm and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint work includes connecting neutral bushing rod of power Transformer and G.I. Earthing strip with the help of flexible copper bond, G.I. Bolt and washer. | item132 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
133 | Fabrication and erection of cable support made of two pieces of G.I. Angle (65x65x6)mm, 2.75 meter long, joined to each other by means of 5 Nos. G.I. Flat (50x6) mm pieces of size 750 mm long each by welding at equal intervals and grouting in a block of size (300x300x700)mm in C.C. 1:3:6 (cement, coarse sand and stone ballast) complete and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint. Work includes providing of three Nos. G.I. clamps made of (50x6)mm G.I. Flat for holding the cable including nuts and bolts. | item133 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
134 | Fabrication and grouting of G.I. frames 3.60 mt. long for support of copper Bus Bar. Bus Bar will be provided in L.V. side of Power transformer. The G.I. frame shall be made of G.I. channel (100x50)mm in ‘T’ shape. Providing 2 Nos. support of G.I. Angle iron (50x50x6)mm, 0.60mt. long below the top channel, drilling of 3 Nos. hole on the top channel for fixing of 11 KV pin insulator and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint and grouting the frame in C.C. ratio 1:3:6 (cement, coarse sand and stone ballast) in a block of size (300x300x700) mm. The work also includes the fixing of 3 Nos. 11 KV pin insulator with pin and binding the copper Bus Bar with the pin insulator by Aluminium binding wire in complete. | item134 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
135 | Providing & Fabrication of copper bus bar of size (2500x50x6)mm in L.V. side of 10MVA 33/11 KV, power transformer, Work includes connection of outside bus bar in L.V. side busing rod of Power Transformer and other side with outdoor 11 KV cable box as well as providing empire tape and H.T. tape etc. for proper insulation work. | item135 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
136 | Installation of 11 KV Switch Gears in Control Room 1 Nos. incoming and 3 Nos. outgoing with one No. Bus coupler. Carefully & safely shifting of 11 KV switch gears from outside to inside the switch gear room grouting foundation of bolts in C.C. ratio of 1:2:4 (including cutting of RCC floor and finishing of RCC floor) as per requirement placing, aligning and fixing of 11 KV anchor GI bolts and nuts of proper size for completion of work. | item136 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
137 | Safely mounting of 11 KV PT on 11 KV incoming switch gear filling of oil (if required) making all electrical connections and testing & commissioning of work. | item137 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
138 | Proper fixing and making bus bar connection in between two switch gears after proper cleaning. Work also include proper insulation, taping by empire, PVC and H.T. tape etc. | item138 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
139 | H.T. Power Cable Laying: Laying 11 KV, (3x300) mm2 XLPE, Cable from power transformer to 11 KV incoming switch gear in the cable trench 0.45 m wide, 0.90m depth. Providing 150 mm local sand for cushion beneath and 150 mm above the cable (quality of local sand required 0.375 cum/m in length). The cable shall be dully protected by brick. On both side of cable by laying brick vertically and bricks would also be laid bricks along the single cable (minimum 18 Nos. of bricks are to be laid top and outer side along the single cable. The work includes digging of trenches, laying of cable in under ground trenches, joining of terminal’s, back filling of earth and testing and commissioning of power cable etc. Spare cable shall be left over and laid in the trenches in shape of 6 m ring at both ends. | item139 | 80 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
140 | Laying and dressing of 11 KV 3x300 mm2 power cable in air/Trench. | item140 | 20 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
141 | Laying 11 KV, 3x185mm2 XLPE, Power cable from outgoing switch gear to 11 KV double poles in the cable trench 0.45m wide, 0.90m depth. Providing 150 thickness mm local sand for cushion beneath and 150mm above the cable (quantity of local sand required 0.375 cubm/m in length). The cable shall be duly protected by brick. On both side of cable by laying bricks vertically and bricks would also be laid horizontally on top of vertically laid bricks along the single cable (minimum 18 Nos. of bricks are to be laid top and outer side along the single cable. The work includes digging of trenches, laying of cable in under ground trenches, joining of terminal’s, back filling of earth and testing and commissioning of power cables etc. Spare cable shall be left over and laid in the trenches in shape of 6m rings at both ends. At the end of feeder cables, where the cable is to be laid across pucca/main road, 100 mm dia G.I. pipe will be weared over the cable in the cable trench for the protection of cable. | item141 | 200 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
142 | Laying and Dressing of 11KV 3x185mm² Power Cable in Air. | item142 | 50 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
143 | Supply and filling of sand in cable trench in the Switch Gear Room. | item143 | 7.8 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
144 | Preparation of 11 KV Power Cable ends: Making of 11 KV XLPE Heat shrinkable outdoor jointing kits after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs | item144 | 5 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
145 | Making of 11 KV XLPE heat shrinkable indoor jointing kits in switch gears after carefully removing the insulation of cable, providing and crimping of proper size of lugs, plumbing and taping of cable with good quality available insulation tape with J/Kit boxes, Fixing and insulating of lugs on cable with switch gear complete in all respect. | item145 | 5 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
146 | Installation of 24V Battery and Battery Charger: Assembling and installation of the cabinet of 24V battery and battery charger in switch gear control room including grouting of foundation bolts as per drawing of manufacture, including providing the foundation nuts and bolts of proper size. The electrical connection between battery and battery charge with flexible copper lead of size 7/20 SWG shall be done properly. The work includes installation, wiring upto control panel, testing and commissioning complete in all respect. | item146 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
147 | Laying of different size of (2x2.5)mm2/ (4x2.5)mm2 control cables i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT’s to CT’s Junction Box, 33 KV CT, 33 KV PT, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item147 | 600 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
148 | Earthing of 11 KV Switch Gears: Preparation of earth mat (Digging of Pits for making bridge on both side of control room by laying 32mm dia M.S.Round in rectangular shape) for earthing of indoor equipments by means of G.I. earth strips (50x6) mm connecting to 4 Nos. earthing electrodes of 32 mm dia. (including fabrications of earthing electrodes) 3m long on either side (as per RESPO drg. RES-40). This work includes driving of earthing electrodes, driving them into earth so that its top remains 500 mm below ground level, earth work, laying bending, welding of G.S. earth strips (50x6)mm and also laying of the G.I. strip (50x6)mm in trench of control room and connecting to both sides squares including cost of G.I. earth strip (50x6)mm approx. 40m length and earthing of all indoor equipment by laying and providing G.I.earth strip (50x6)mm including cutting & welding etc. | item148 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
149 | Lighting Arrangement of 33/11 KV S/S outdoor switch yard and its area: Supply & installation and erection of 6 Mtr. Long street light supports with 2.4 feet long street light brackets including fixing and supply of junctions box, street light support shall be made and fabricated from G.I. pipe of 3.0 Mtr. Long 100mm dia. And 3.0 Mtr. Long 75mm dia with 2.4 Mtr. Long street light bracket in arc shape and made up of 40 mm dia G.I. pipe. Grouting of support in C.C. ratio 1:3:6 (cement, core sand and stone ballast) in size (0.40x0.4x1.2)m, Lightning poles shall also be earthed by connecting to earth mat. | item149 | 8 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
150 | Supply and Fixing of LED light 120 W and of standard quality ISI mark with water tight elbow fitting etc. complete in all respect and suitable for above street light supports (Acceptable make Philips, Bajaj, Heawels or Siska). | item150 | 8 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
151 | Laying of 3½x70 mm2 PVC LT cable from 11/0.4 KV, 63 KVA T/F to L.T. distribution board in switch gear room after digging trench for laying cable and refilling of trench including connections at both ends after providing and crimping of lugs of proper size for completion of work and laying brick over & both sides of L.T. cable after digging trench of 0.3 m wide & 0.5 m depth and providing and wearing 75 mm dia G.I. pipe of 2.5 M length over L.T. Cable complete in all respect. | item151 | 20 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
152 | Laying of 3x50mm2 11KV cable from 11KV outgoing VCB in control room to PCC Double Pole after digging trench for laying cable and refilling of trench including connections at both ends after providing and crimping of lugs of proper size for completion of work and laying brick over & both sides of 11KV cable after digging trench of 0.3 m wide & 0.5 m depth and providing and wearing 75 mm dia G.I. pipe of 2.5 M length over 11KV Cable complete in all respect. | item152 | 50 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
153 | Erection of L.T.Aluminum XLPE insulated cable 1x50mm2 for jumpering on Double Pole. | item153 | 30 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
154 | Providing and Lightning arrangement of 33/11KV S/S control room (8 No. ceiling fans of preferable make Havels, Crompton & Bajaj), (20 No. 12 Watt Led bulb with fitting if required preferable make Philips, Crompton, Havels & Bajaj) | item154 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
155 | Fabrication of L.T. distribution board by using G.I. Angle size (65x65x6)mm of size (2x0.75x1.4)m and grouting the stand in ground floor in switch gear room at proper place. 12 mm thick Indian wooden ply with sunmica top will be fixed on the ply frame and frame will be painted by one coat of primer red oxide and two coats of smoke grey paint. | item155 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
156 | Providing & Fixing 100amp TPN MCCB, 4 Pole and 4 nos. 32amp single phase, MCCB in box as per catalogue no. 607780 ligrant make or equivalent. | item156 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
157 | Providing and laying (2x6)mm2 L.T. Aluminium PVC cable from S.G. Room to street light supports after digging of trench laying of (2x6)mm2 cable, providing brick on top of cable, refilling of trench, making connections of poles with street light fitting through junction box complete in all respect. | item157 | 110 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
158 | Construction of 11 KV Feeder Double Poles: Erection and grouting of 2 Nos. STP-55-11Mtr long for making DP Structure including fabrication fixing of G.I. Channel, G.I.Angle, TPMO, Fuse Set, disc, insulators, pin insulators No. Plate, Danger board, barbed Wire (02 Kg per Pole) etc. the work includes supply and fixing of necessary clamps size 75x10mm with G.I.Nuts bolt & washer, bolts and washers. The work also includes grouting of Double pole support in C.C. 1:3:6 (cement, Core sand & stone ballast) in block of size (0.45m x 0.45 x 1/6 length of the pole) including earthing of Double pole with G.I. earthing rod complete in all respect. | item158 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
159 | Providing & wearing of 110 mm dia 3.5 mm long G.I. pipe in the feeder cable of size of (3x185/3x300)mm2 XLPE 11KV power cable before making the outdoor cable boxes. The work includes the sealing of G.I. Pipe, top end and lower end of the pipe is to be buried in to the ground about ½ m and proper dressing of cable etc. The work includes lifting, mounting and clamping of 11 KV feeder cable boxes on the feeder with double pole structure and making connections including supply of cable mounting clamps etc. | item159 | 6 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
160 | Erection of ACSR Weasel Conductor for jumpering on Double Pole | item160 | 100 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
161 | Providing & fixing of SMC Danger board at each location as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt for 11KV | item161 | 7 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
162 | Grouting of stay rods (16x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. | item162 | 8 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
163 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 11KV and Stay Clamps. | item163 | 8 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
164 | Erection and grouting of 2 Nos. PCC 9.0Mtr long for making DP Structure including fabrication fixing of G.I. Channel, G.I. Angle, TPMO, Fuse Set, pin insulators No. Plate, Danger board, barbed Wire (01 Kg Per Pole) etc. the work includes supply and fixing of necessary clamps with nuts, bolts and washers. The work also includes grouting of Double pole support in C.C. 1:3:6 (cement, sand & stone ballast) in block of size (0.45m x 0.45 x 1/6 length of the pole) including earthing of Double pole with G.I. earthing rod complete in all respect. | item164 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
165 | Plinth of Substation T/F with RCC Top of size 2x2x1.6 Mtr. Incl. 2 nos. G.I. Channel of 125x65x6mm as per specification | item165 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
166 | Installation of 11/0.4 KV, 63 KVA T/F on Plinth and providing and fixing of Lugs & copper L-piece (04 No.) of size 400x50x6mm on LT bushing Rod of S/s T/F and making of 11 KV & L.T.Connections of Transformer complete including earthing of T/F with chemical Pipe earthing the work in all respects. | item166 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
167 | Installation of 33 KV Isolators: Assembling and installation of line/Bus Isolator on the isolator structure. Adjusting of operating mechanism in proper alignment so as to ensure smooth operation of the same. In case of Line Isolator proper operation of earth links shall also be ensured. The work includes fabrication for proper fixing if required. | item167 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
168 | Installation of 33 KV Lightning Arrestors: Assembling and installation/mounting of 3 Nos. lighting arrestors on the L.A.’s structure/terminal gentry, complete with earthing and line connections. The work includes fabrication for proper fixing, if required. | item168 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
169 | Installation of 33 KV Post Insulators: Installation of 6 Nos. PI on structure. The work includes fabrication for proper fixing, if required. | item169 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
170 | Installation of 33 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure. The work includes fabrication for proper fixing, if required. | item170 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
171 | Installation of 33 KV VCB Assembling and installation of 33 KV VCB on the VCB out door structure on the plinth. Adjustment of operating mechanism in proper alignment for smooth operation of the same. The work also includes fabrication of addition arrangement for proper fixing, if required. | item171 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
172 | Installation of 33 KV VCB Control Panel for single feeder & Double T/F Control Panel. Carefully and safely shifting of 33 KV VCB control panel from outside of the switch gear room to inside of the switch gear room, grouting with anchor bolts in the floor, work also includes cutting & proper finishing of floor if necessary for completion of work. Placing and fixing of panel on foundation, bolts of proper size in proper position and alignment. | item172 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
173 | Installation of 33 KV C.T.’s: Installation of 3 Nos. C.T.’s on the C.T’s structure. The work includes fabrication for proper fixing, if required to complete the work. | item173 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
174 | Installation of 33 KV P.T.’s: Installation of 3 Nos. P.T.’s on the P.T’s structure. The work includes fabrication for proper fixing, if required to complete the work. | item174 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
175 | 33 KV CT’s Junction Box: Providing & fixing of junction box of size (400x400x150) mm made of G.I. sheet of 16 SWG in between 33 KV CT’s & control panel. The work also include making proper connection on the junction box and making all connection in between CT’s and control panel complete as per manufacture’s panel drawing including testing and commissioning of work etc. complete the work. | item175 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
176 | 33 KV Bus Bar Jumpering: Jumpering, including clamping/binding with ACSR Panther conductor/33KV 3x300mm2 XLPE cable with providing P.G.Clamp & other accessories. Terminal Gantry to 33KV P.T | item176 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
177 | 33KV P.T to 33 KV P.I | item177 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
178 | 33 KV P.I to 33KV L.A | item178 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
179 | 33 KV L.A to 33 KV Line isolator | item179 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
180 | 33 KV Line isolator to 33 KV VCB | item180 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
181 | 33 KV VCB to 33 KV C.T | item181 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
182 | 33 KV C.T to 33 KV P.I | item182 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
183 | 33 KV P.I to 33/11 KV P.I | item183 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
184 | 33 KV Post insulator to Bus isolator. | item184 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
185 | 33KV Bus isolator to 33KV VCB | item185 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
186 | 33KV VCB to 33KV CT | item186 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
187 | 33KV CT to 33KV Fuse set | item187 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
188 | 33KV Fuse set to 33KV L.A | item188 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
189 | 33KV LA to 33/11KV 10MVA T/f | item189 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
190 | Tripping, Single line diagram, Board: Providing & fixing of single line diagram board for 33/11 KV substantions of size (1200x900)mm made of Indian Plywood 6 mm thick fitted on wooden frame made of Sal wood of size (50x30)mm. Two support of Sal wood of size 1200 mm and two supports of size 900 mm shall be tapered on the front side and properly finished, the board shall painted with white enamel paint in two coats after one coat of primer shall be used in both side. The prescribed matter/chart shall be written neatly with red, green and black paint as required & providing 04 Nos. copyes of layput of substation after survey on A-2, Paper. | item190 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
191 | Fabrication, Erection & Grouting of 33/11KV S/S Name Board of size (0.75x1.5) Mtr 2.40Mtr high frame of G.I. Angle of size 50x50x6mm, Two cross Bracing of G.I. Flat of size 25x6mm shall be fixed with frame, Board shall be made of 18SWG G.I. sheet of size .75x1.5mtr shall be fitted in frame with Rivit Board letter should be written by black paint on yellow back ground Providing All required materials by the contractor own his cost. | item191 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
192 | Supply & fixing of Aluminium clamps such as Isolator, LA, Transformer end clamp, fuse set, post insulator, PG clamp etc. complete with nut, bolt & washer for Dog / Panther Conductor | item192 | 72 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
193 | To provide required No. of technicians to work on power T/f, HT/LT panels & 33KV line during testing as assisting technical hands of test team during commissioning & energisation. | item193 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
194 | Earth filling in switch yard including cost of earth obtained from out side PVVNL property its carriage upto 25 Km watering ramming of earth is 50 cm layers complete in all respects. | item194 | 320 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
195 | Levelling & Dressing of the switch yard including cutting up rooting of grass/grass leveling on making proper slope watering & ramming. The work also includes removal disposal rutatst out of S/S area. | item195 | 320 | Sqmt | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
196 | Making plinth of D/P & street light, support in CC 1:3:6 of size 45 cm dia & .30 mtr. In height complete with all labour T&P etc. | item196 | 14 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
197 | Construction of SSO’s approached road 1.2 Mt wide in switch yard by laying dry brick ballast in 15 cm layer, 115 mm thick brick work 1:4 in both side of edge, providing 10 cm thick CC in ratio 1:2:4. The work include proper plastering top & side of road and making groove, leveling & dressing of earth beneath the brick work on edge. All required materials provived / supply by the contractor own his cost. | item197 | 30 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
198 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, Stone Pad Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as an fabrication work if required. Single Pole (a) 11M Long STP, SP-55 Round Pole | item198 | 160 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
199 | (b) 13M Long STP, SP-72 Round Pole | item199 | 13 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
200 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) 11M Long STP, SP-55 Round Pole | item200 | 19 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
201 | (b) 13M Long STP, SP-72 Round Pole | item201 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
202 | End Double Pole Structures (a) 11M Long STP, SP-55 Round Pole | item202 | 18 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
203 | Riser Double Pole The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all clamps size (65x8mm), Nut bolt & Washer, Stone Pad, Lugs, Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports & hardware material from sectional store to pit site as well as an fabrication work if required. Fixing of 04 Nos. G.I.Channel 100x50x2.4Mtr (With arrangement of 06 Nos. 33KV Pin insulator with Pin). The work also includes cutting of channel/angles, making holes on G.I.Channel / G.I. Angle, spring washer of proper size for channel/angle. Contractor also provide G.I.Channel clamps and E- clamps at his own cost as per Respo Norms. (a) 11M Long STP, SP-55 Round Pole | item203 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
204 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per drawing. Work includes back filling and proper ramming. Single Pole (a) 11M Long STP, SP-55 Round Pole | item204 | 160 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
205 | (b) 13M Long STP, SP-72 Round Pole | item205 | 13 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
206 | Double Pole Structures (a) 11M Long STP, SP-55 Round Pole | item206 | 19 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
207 | (b) 13M Long STP, SP-72 Round Pole | item207 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
208 | End Double Pole Structures (a) 11M Long STP, SP-55 Round Pole | item208 | 18 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
209 | Riser Double Pole (a) 11M Long STP, SP-55 Round Pole | item209 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
210 | Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. | item210 | 304 | Set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
211 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 33KV and Stay Clamps. | item211 | 304 | Set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
212 | Providing & Earthing of supports with G.I. earth Rod of (20x2500)mm long including excavation of pit and driving G.I.Rod 3.0M apart from suppor and 0.5M below the ground level and connecting belowl the earth electrodes with the help of G.I.wire No.8SWG, G.I.Nut bolt & washer and earthing lugs. | item212 | 267 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
213 | Laying, spreading, lifting and final sagging of 3 phases ACSR Dog conductor in accordance with Line chart includidng binding and fixing of all accessories in 03Nos. Conductor in parallel. | item213 | 24.754 | Km. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
214 | Making Jumpers on Sectional Pole, by providing & fixing of P.G.Clamps of proper sizes, suitable for Dog Conductor/ 33KV, 3x300Sq.mm XLPE cable. Sectional Double Pole | item214 | 20 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
215 | End Double Pole | item215 | 18 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
216 | Riser Double Pole | item216 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
217 | Guarding between two poles like single poles, double poles, four poles, etc. to guard L.T., 11KV Line telephone line and river crossing, road crossing etc. with G.I.wire No.6SWG, G.I.wire No.8SWG and G.I.wire No.16SWG including cutting with fabrication and fixing of G.I.Guarding angle 75x75x6mm with Providing & fixing G.I.clamps size 75x10mm, G.I.Turn buckle, G.I.Eye bolt, nut bolts & washer etc, as per drawing. | item217 | 100 | Per Span | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
218 | Providing & fixing of SMC Danger board at each location as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt for 33KV | item218 | 221 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
219 | Providing & fixing of SMC Number Plate at each location as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt. | item219 | 219 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
220 | Chopping of branches of trees of eucalyptus, Neem, Keekar and other kind of trees along the route of the line and disposal of the same at suitable place. | item220 | 6.982 | Per Km. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
221 | Making H.T.Connection of the proposed line from 33KV Line. The work consists of fixing & fabrication of Dropper Channels, & fixing of Disc Insulators, Pin Insulators, jumpering with P.G.Clamps, clamping and binding etc,as per site conditions. | item221 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
222 | Providing & Wrapping of barbed wire (2.0Kg per Pole) on 33KV ST Poles SP-55/SP-72 as anti-climbing device for a length of 0.9Mtr. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a height of 2.75Mtr. from the ground, complete with providing and fixing of lower end & upper end clamps made of G.I.Flat 40x5mm complete with nuts&bolts. | item222 | 259 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
223 | Painting of following supports/structures of 33KVLine, with two coats of synthetic enamel aluminium paint after one coat of ready mix primer, including cost of all material, as well as rubbing/cleaning of surface as required for proper completion of work:- 11Mtr SP-55 Poles including all channels/x-arms/clamps etc. (i) Single Supports | item223 | 160 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
224 | (ii) Double Pole Structure | item224 | 19 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
225 | (iii) Cable Riser | item225 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
226 | (iv) End Pole | item226 | 18 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
227 | 13Mtr SP-72 Poles including all channels/x-arms/clamps etc.: (i) Single Supports | item227 | 13 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
228 | (ii) Double Pole Structure | item228 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
229 | Digging of Trench by excavation of earth of 1050x750mm size for 33KV line | item229 | 1059 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
230 | Safe laying of 33KV, 3x300Sq.mm. XLPE Cable in Cable Trench to respective Double Pole. | item230 | 1059 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
231 | Providing & Laying of Ist Class Bricks, along the length on both side of 33KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr per Cable) and Stone Slab of size 450x600x50mm on top of the each Cable, Providing 150 thickness mm River sand for cushion beneath and 150mm above the cable as per specification. | item231 | 1059 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
232 | Back filling of excavated earth in the cable trench upto the ground level and ramming properly. | item232 | 1059 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
233 | Supply & Laying of 33KV, 3x300Sq.mm XLPE cable in HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item233 | 2574 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
234 | Laying of 33KV, 3x300Sq.mm XLPE cable in HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item234 | 2574 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
235 | Laying of 33KV, 3x300Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing trench cable trench, nala x-ing & G.I.Pipe and making connection with 33KV over head line at both ends. | item235 | 362 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
236 | Providing & Fixing 150mm dia 2mm thick 3M long G.I.Pipe over 33KV, 3x300Sq.mm XLPE Cable before mounting the 2No. Cable on double pole. Work includes fixing of Clamp, sealing of top and bottom end of the G.I.Pipe. One end of G.I.Pipe is to be buried under earth about 500mm. | item236 | 28 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
237 | Making of 33KV Outdoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item237 | 40 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
238 | Making of 33KV Straight through Cable Jointing Kits 3x300mm² and crimping of proper size aluminium lugs. Work includes providing insulating tapes etc as per specifications. | item238 | 3 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
239 | Providing, Fixing & Laying of G.I.Pipe 150mm Dia thickness at Nala X-ing Work includes G.I.Clamps, Nut bolt & washer, bricks, cement, sand & stone grift etc. | item239 | 12 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
240 | Supply & fixing of cable route marker along the route of 33KV cable with proper grouted with proper painting & marking PVVNL, 33KV HT Cable. | item240 | 30 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
241 | Road restoration charges for 1Mtr wide Kuccha Road (Inter locking Tiles, Bricks Road & Developed green belt only). | item241 | 300 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
242 | Road restoration charges for 1Mtr wide Pucca Road (Cemented, Concrete & Black road only). | item242 | 200 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information