## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : Energisation of Underground 11KV and LT Network of Block F, G and H Sector – 44 under SDO – XII, Noida in jurisdiction of EUDD-III,. Noida.
Contract No: SHORT TERM E-TENDER NO 10/EUDC-II NOIDA/2023-24
G.S.T. paid extra as applicable
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) The rate quoted by the tenderer shall be inclusive of all duties, taxes (except GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. GST AND ALL TAXES INCLUSIVE IN QUOTED RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder INCLUSIVE OF ALL TAXES AND GST Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with All Taxes and GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Energisation of Underground 11KV and LT Network of Block F, G and H Sector – 44 under SDO – XII, Noida in jurisdiction of EUDD-III,. Noida | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe Carriage of Line Accessories and items releated to work issued from store - 4050Mtr. 11KV 3x185sqmm XLPE Cable, 19 Nos. 11KV Cable Jointing Kits, 1650mtr. 3.50x240sqmm LT XLPE Cable, 3.5x240sqmm LT XLPE Cable Straight Through, 25500mtr 4x50sqmm LT PVC XLPE Cable and any other items/accessories required for work rom Store Centre Sahibabad/Noida/Ghaziabad/Meerut/Any Store of Discom PVVNL/UPPCL to work site including safe loading and unloading at both ends. (Material Qty. are mentioned in Tender Documents.) |  | 1 | Ton | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | Drilling of dia 220 mm in two parallel bores for Double Curcuit by trenchless method by horizontal boring machine at a depth of 1.50 mtrs to 2.50 mtrs. (as requirement at site) below the ground level with complete work in all respect as per RESPO. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 3050 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | Supply of 160mm OD PN-4 PE 80 Grade UV Stabilized HDPE Pipe as per PVVNL GTP approved. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 3050 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | Laying and interconnecting of above HDPE pipe in Trench for laying of Double Ckt. 11KV 3x185sqmm XLPE Cable, as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 3050 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop and making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 19 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | Laying, pulling, Hosting and Commissioning of Double Ckt. 11KV 3x185sqmm XLPE Cable in HDPE pipe by HDD trenchless method with making risers at poles, complete work in all respect as per RESPO. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 3050 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | Laying, pulling and comissioning of 11 KV size 3x185 Sqmm XLPE Double Ckt. by manual method with Laying of parallel 11KV 3x185sq mm XLPE cable by digging of trench of size 750 mm wide 1050 mm deep and boxing with brick by three sides, sand, stone slab 600x450x50mm & providing of hume pipe 160 mm dia its required filling of trench, leveling and proper rooming as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1000 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | Fixing, making and Comissioning of 11KV Outdoor Cable jointing kits suitable for 11KV 3x185sqmm XLPE Cable with the help of Jointer and complete connections in all respect. (Outdoor Cable Jointing Kits shall be provided by the deptt. and work including crimping lugs, insulating tapes etc. in the scope of contractor). |  | 1 | Job | 100 |  |  | Excess(+) | 19 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Supply of rigid PVC Pipes (Size 160mm OD x thickness 6.1mm x 2.5mtr long as per PVVNL GTP approved. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | Laying, Pulling, looping and comissioning of LT XLPE Cable 3.5x240sqmm in double Ckt. by manual method with Laying of parallel of above cable by digging of trench of size 750 mm wide 1050 mm deep and boxing with brick by three sides, sand, stone slab 600x450x50mm in PVC Pipe (Size 160mm OD x thickness 6.1mm x 2.5mtr long) with filling of trench, leveling and proper rooming as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1650 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Fixing, making and Comissioning of LT Straight through suitable for LT 3.5x240sqmm XLPE Cable with the help of Jointer and complete connections in all respect as per site requirement. (LT Straight through shall be provided by the deptt. and work including crimping lugs, insulating tapes etc. in the scope of contractor). |  | 1 | Job | 100 |  |  | Excess(+) | 25 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Laying, pulling and comissioning of 4x50sqmm LT PVC XLPE Cable by manual method by digging of single trench of size 250 mm wide, 400 mm deep and boxing with brick by three sides, sand, stone slab & providing of hume pipe 200 mm dia its required filling of trench, leveling and proper rooming as per site requirement. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 25500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Supply and Fixing of Missing Part 990KVA Distribution T/f, HV, LV Bus Bar, Nut Bolt and Missing part of LT Distribution Box as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 64 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Complete Overhauling of 990KVA T/F with HV & LV sides switchgears and Protection. |  | 1 | Nos. | 100 |  |  | Excess(+) | 24 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Complete Chemical Earthing of LT Distribution Panel as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | Water Lavel Earthing as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 24 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Dismentaling of old and damaged overhead HT Line and safe carriage from work site to any store of PVVNL Discom including loading & unloading both sides. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 4500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Dismentaling of old and damaged overhead LT Line and safe carriage from work site to any store of PVVNL Discom including loading & unloading both sides. |  | 1 | Mtr. | 100 |  |  | Excess(+) | 9500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Dismentaling of old and used ST Pole 13mtr long and safe carriage from work site to any store of PVVNL Discom including loading & unloading both sides. |  | 1 | Nos. | 100 |  |  | Excess(+) | 105 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | Dismentaling of old and used LT Pole 9mtr long and safe carriage from work site to any store of PVVNL Discom including loading & unloading both sides. |  | 1 | Nos. | 100 |  |  | Excess(+) | 107 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Dismentaling of old and Damaged 04 Nos. 990KVA T/F outer body scrap and 800kg. Iron Scrap channel and other item with safe carriage from work site to any store of PVVNL Discom including loading & unloading both sides. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information