## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer Electricity Distribution Circle-II, Saharanpur
Name of Work: fo¦qr forj.k [k.M&jkeiqj efugkju] lgkjuiqj ds vUrxZr midsUnz ukukSrk&f}rh; ds {ks= esa jktdh; tu fo’ys”kd iz;ksx’kkyk] jsyos jksM] ukukSrk gsrq iw.kZ tek ;kstuk ds vUrxZr 300 ds0oh0,0 okf.kfT;d l;ksatu fuxZr djus ds dk;ZA
Contract No: 23/W/EDC-II/SRE/2024-25
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )Inclusive of GST
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Qty. |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE (Inclusive of GST) In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT Inclusive of GST | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 4 | 7 | 8 | 9 | 10 | 11 | 12 | 5 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 6 | 54 | 7
1 | Detail of Work | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Safely carriage of ST poles SP-55 11 Mtr. long from ESC, SRE/JE store to site of work at various sites including loading & unloading at both ends. |  | 7 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Safely carriage of other complete line material (Except ST Poles ) from ESC, SRE /JE store to site of work at various sites including loading, unloading at both ends. |  | 3 | Ton. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | Safely carriage of 11 KV XLPE cable of size 3x120 sq mm. from ESC, SRE/JE store to site of work at the sites including loading & unloading at both ends. |  | 2300 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.04 | Safely carriage of 630 KVA T/F from ESC, SRE/JE store to site of work at various sites including loading & unloading at both ends. |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.05 | Safely carriage of 11 KV Pilfer proff metering cubical from ESC, SRE/JE store to site of work at the sites including loading & unloading at both ends. |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.06 | Safely carriage of 11 KV outgoing VCB from ESC, SRE/JE store to site of work at various sites including loading & unloading at both ends. |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.07 | Erection of Single support on ST poles 11 Mtr Long with complete fitting with all accessories. |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.08 | Erection of Double support on ST poles 11 Mtr Long with complete fitting with all accessories. |  | 3 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.09 | Earthing of poles by earthing rod. |  | 7 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.1 | Concreting of ST poles SP-55, 11 Mtr. long with cement concreting in bolck of 600X600X1500 MM. in ratio 1:4:8 with cement, sand and brick ballast size 1''x1.5'' with plinth. |  | 7 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.11 | Concrating of stay rods by digging of pits in block of 600X600X300 mm. & with new brick and nozzling of stay wire 7/10 SWG and fitting the same on the pole |  | 10 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.12 | Providing of nuts & bolts off size. |  | 10 | Kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.13 | Providing and fixing of All Type clamps for ST poles made of new MS flat size 50x6 mm with nut bolts. |  | 30 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.14 | Providing of HDPE pipe 3 mtr. long 6" dia |  | 10 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.15 | Fixing of HDPE pipe 3 mtr. long 6" dia |  | 10 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.16 | Constriction of plinth for installation of 630 KVA T/F of size 5x5x4 ft. of 9" inch thick wall in all four sides with 6”inch thick RCC Top duly filled with sand and plastered 12mm thick in ratio 1:4 with cement and sand on outer surface of brick wall as per RESPO Specification. |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.17 | Water level Earthing of 630 KVA T/F (1 No body & 1 No. neutral earthing) by boring 60 fit deep with providing & fixing of G.I pipe 1½” Dia (Jindal Class B) and connecting with G.I. Strip of size 40x5 mm and G.I wire at bottom of G.I pipe to the T/F providing of required charcoal & salt in the pipe |  | 2 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.18 | Wiremesh fencing 630 KVA T/F size 6x6x5 mtr with grouting making frame of MS angle 40x40x6 mm and fixing four no ms strip size 25x6 mm at equal distance in between the frame and fixing square mesh of 50 mm squre in each frame the fencing should cover all side of T/F with providing 1 no door size 6x3 with sitakni & dandala with green paints (British/Asian/enamel paints) |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.19 | Fixing of 11 KV polymeric pin Insulator. |  | 6 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.2 | Making the trench for 11 XLPE cable 3x120 sq mm. |  | 1100 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.21 | Laying of 11 KV XLPE cable 3x120 sq.mm. in to the trench after spreading the sand into the trench and then laying of Ist class bricks into the trench and put the cable on the bricks and then covered the cable with Ist class bricks from all three sides of cable and then filling the earth with ramming. |  | 2200 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.22 | Erection of 11 KV XLPE cable 3x120 sq mm in AIR on new double pole. |  | 100 | Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.23 | Fixing of 11 KV indoor Jointing kit size 3x120 sq mm |  | 8 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.24 | Fixing of 11 KVoutdoor Jointing kit size 3x120 sq mm |  | 10 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.25 | Safely installation of New 630 KVA T/F on the plinth with proper alignment and Complete fitting including making connection and commissioning |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.26 | Installation of pilfer metering cubical 20/5 A |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.27 | Installation of 11 KV VCB outgoing. |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.28 | Connection of New VCB outgoing and earthing with existing earthing system. |  | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.29 | Fixing of MS channel 100x50x6 sq.mm (2 No. dropper and 2 No top) |  | 4 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.3 | Installation of 11 KV TPMO with polymer insulator |  | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
1.31 | Choping of tree branches touching the 11 KV line |  | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information