PRE QUALIFYING CONDITIONS

These pre qualifying requirements (PQR) shall prevail over the pre qualifying conditions mentioned in instructions to tenderer’s or anywhere in the tender document.

- FOR REGULAR SUPPLIERS:

- Manufacturer: The tenderers shall themselves be manufacturers of 33 KV metering cubicles.

- Turnover Requirement: The bidder should have a minimum average annual turnover of Rs. 05 (Five) crore for best three years out of last five financial years. The audited balance sheet/CA’s certificate shall be enclosed in support of above, failing which the bid shall not be considered.

- Manufacturing experience: The tenderers must have experience of supplying 50% of tendered quantity in best 03 (three) years out of last 05 (five) years to Government/ government undertaking/ power utilities companies directly or through EPC contractor failing which their offer part-II (price bid) may not be considered for opening

Table- PE

| Year | Complete postal address including designation of authority placing order | Order no. & date | Quantity Ordered Nos.) (Similar ratings and higher rating) (for each item) | Qty. supplied during the year ( Similar ratings and higher rating) (for each item) | Balance quantity to be supplied against orders in hands |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |

The copy of purchase orders & DIs are to be enclosed with offer in support of manufacturing & supply experience otherwise offer may not be considered.

- Operational experience: The manufactured quantity of the tendered equipment should have given proven trouble free operational service for the last three years in tropical climate prevailing in India.

5.   Testing Facilities:

The tenderer must have all necessary facilities at their works for carrying out such routine and acceptance tests as prescribed in the relevant ISS and any other routine and acceptance test as specified in the specification. Documentary evidence of existence of such facilities will be filed along with the tender.

6.      Type Test:

  - For indigenous bids or fully imported bids:

    - Certified copies of all type tests as per relevant IS-2705-1992, IS:3156-1992 with latest amendments listed below obtained from any Third Party Govt. Lab CPRI/ERDA on similar equipment's included in this specification shall be furnished along with tenders The type test reports shall not be older than 07 (Seven) years from the date of opening of tender. (As per CEA Guideline for the validity period of type test of Government of India, Ministry of Power in May 2020 & UPPCL Order No. 4115/Respo/Saubhagya/Quality Cell Dated 09.12.2021) : –

CT:

- Short time current test

- Lightening impulse test

- Temperature rise test

- High voltage power frequency wet withstand voltage test

- Determination of errors or other characteristics according to the requirement of the accuracy class.

- Instrument security current test.

PT:

a)	Determination of error according to the requirements of 	accuracy class.

b)	Temperature rise test.

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

c)	Impulse Voltage Test.

Complete metering cubicle: The complete metering cubicle after fitting all CTs and PTs shall be type tested for impulse test by CPRI/ERDA test lab. The type test report shall be submitted by the bidder.

6.1.2	Bidder shall furnish the calculation of short time thermal current of all ratios of offered equipment in the tender, on the basis of cross-sectional area of primary conductor of type tested equipments.

6.1.3 If the firms are meeting the eligibility criteria as above but do not have valid type test report for offered equipment as per current technical specification with revised parameters as prescribed by PVVNL for cross sectional area of conductor, core, current density, the firm shall have to give undertaking to submit valid type test report of offered equipment issued by CPRI/ERDA only within maximum period of three months' time. Keeping in view of the timely completion of projects supplies shall be accepted, with the provision that 80% payment shall only be released and the balance 20% may be released only after submission of valid type test report.

6.2     	For indigenous bids under valid foreign collaboration.

6.2.1 	The offered indigenously manufactured or collaborators manufactured equipment should have been type tested and report submitted with the tender.

6.2.2	The collaborator's equipment shall have three years operating experience under tropical climate.

7.    	The tenderers are required to offer minimum 100% of tendered quantity & this clause shall supercede any other clause regarding minimum quantity to be quoted, if mentioned anywhere else.

- Guarantee Period:The units shall be guaranteed for a period of 42 months from the date of receipt of material at site or 36 month from the date of commissioning whichever is earlier. During the guarantee period bidder shall be responsible for free replacement at site for any defect/damage reported by the purchaser. The defective/damaged equipment should be replaced with in five days of intimation of damage by the purchaser, failing which a penalty of Rs.200 per day, to the maximum limit of cost of new equipment for similar capacity, shall be deducted from the firm’s bill or security for the delayed period. Clause 30 of General Conditions of contract Form B shall be treated as amended to that extent.

- COMPARISON OF RATES:

As per UPPCL OM  No.857(i)/ dk;Z@pkSng&ikdkfy@2013&29 ds@83 Vh0lh0&2 ¼2012½ fnukad 11-10-2013 the comparison of rates shall be done on the basis of Ex-works rates+Freight,  excluding Excise duty and VAT etc.

- FOR TRIAL SUPPLIERS:

Purchase at his discretion may consider to award trial order, only if regular suppliers are not available in sufficient number and there seems to be lack of competition.

- Manufacturer: The tenderers shall themselves be manufacturers of 33 KV metering cubicles.

- Turnover Requirement: The bidder should have a minimum average annual turnover of Rs. 2.50 crore for best three years out of last five financial years. The audited balance sheet/CA’s certificate shall be enclosed in support of above, failing which the bid shall not be considered.

- Manufacturing & operational experience:

Tenderer must have manufactured and supplied 25% of tendered quantity in best 03 (three) years out of last 05 (five) years to Government/government undertaking/ power utilities directly or through EPC contractor. The copy of purchase orders & DI are to be enclosed with offer in support of manufacturing & supply experience otherwise offer may not be considered.

- Operational experience: The manufactured quantity of the tendered equipment should have given proven trouble free operational service for the last one year in tropical climate prevailing in India.

Table- PE

| Year | Complete postal address including designation of authority placing order | Order no. & date | Quantity Ordered (Nos.) (Similar ratings and higher rating) (for each item) | Qty. supplied during the year ( Similar ratings and higher rating) (for each item) | Balance quantity to be supplied against orders in hands |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |

5. Testing Facilities:

The tenderer must have all necessary facilities at their works for carrying out such routine and acceptance tests as prescribed in the relevant ISS and any other routine and acceptance test as specified in the specification. Documentary evidence of existence of such facilities will be filed along with the tender.

6.      Type Test:

For indigenous bids or fully imported bids:

6.1.1  Certified copies of all type tests as per relevant IS-2705-1992, IS:3156-1992 with latest amendments listed below obtained from any Third Party Govt. Lab CPRI/ERDA on similar equipment's included in this specification shall be furnished along with tenders The type test reports shall not be older than 07 (Seven) years from the date of opening of tender. (As per CEA Guideline for the validity period of type test of Government of India, Ministry of Power in May 2020 & UPPCL Order No. 4115/Respo/Saubhagya/Quality Cell Dated 09.12.2021) : –

- Short time current test

- Lightening impulse test

- Temperature rise test

- High voltage power frequency wet withstand voltage test

- Determination of errors or other characteristics according to the requirement of the accuracy class.

- Instrument security current test.

PT:

a)	Determination of error according to the requirements of accuracy class.

b)	Temperature rise test.

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

c)	Impulse Voltage Test.

Complete metering cubicle: The complete metering cubicle after fitting all CTs and PTs shall be type tested for impulse test by ERDA or CPRI test lab. The type test report shall be submitted by the bidder.

6.1.2	Bidder shall furnish the calculation of short time thermal current of all ratios of offered equipments in the tender, on the basis of cross-sectional area of primary conductor of type tested equipment.

6.1.3	If the firms are meeting the eligibility criteria as above but do not have valid type test report as per current technical specification with revised parameters as prescribed by PVVNL for cross sectional area of conductor, core, current density, shall have to give undertaking to submit valid type test report of offered equipment issued by CPRI/ERDA only within maximum period of three months' time. Keeping in view of the timely completion of projects supplies shall be accepted, with the provision that 80% payment shall only be released and the balance 20% may be released only after submission of valid type test report.

6.2     For indigenous bids under valid foreign collaboration.

6.2.1 The offered indigenously manufactured or collaborators manufactured equipment should have been type tested and report submitted with the tender.

6.2.2 The collaborator's equipment shall have three years operating experience under tropical climate.

7. 	One sample of 33 KV Metering Cubicles randomly selected from each offered lot shall be opened for verifying the diameter & cross sectional area of primary coil conductor including verification of GTP. The sample so selected shall be at the cost of supplier

- Additional Guarantee Period: The Cubicles supplied by trial supplier shall be guaranteed for additional 24 months from the Guarantee period applicable for regular supplier which is 42 months from the date of receipt of material at site or 36 month from the date of commissioning whichever is earlier. This clause supersedes all the other clauses regarding guarantee period mentioned anywhere in the tender. During the guarantee period bidder shall be responsible for free replacement at site for any defect/damage reported by the purchaser. The defective/damaged equipment should be replaced with in five days of intimation of damage by the purchaser, failing which a penalty of Rs. 200 per day, to the maximum limit of cost of new equipment for similar capacity, shall be deducted from the firm’s bill or security for the delayed period. Clause 30 of General Conditions of contract Form B shall be treated as amended to that extent.

The price bid of trial firm shall not be opened but the firm has to submit their price bid online so as to complete the e-tendering process. In case of award, the firm may be offered rates as approved by the purchase committee for lowest regular supplier.

NOTE: This above mentioned PQR shall prevail over PQR mentioned elsewhere in any place in these tender documents. All instruction and terms and conditions of instruction to tenderers and Form B other than mentioned above shall remain unchanged.

- CT: It is also  proposed to having following  values of current density for CTs -

- Current density at rated current(max)	- 1.5 Amp. Per sq. mm

- Current density at STC for 1 sec(max) - 165 Amp. Per sq. mm.

- Cross sectional area of primary Should be as per  rated current density or as per current density at STC (for 1 second) whichever is higher.

- PT: The cross sectional area of primary should be 0.04 sq. mm(Minimum) and that of secondary winding should be 1.6 sq. mm (Minimum).

- One sample of 33 KV CT/PT randomly selected from each offered lot shall be opened for verifying the diameter & cross sectional area of primary coil conductor including verification of GTP. The sample so selected shall be at the cost of supplier.

Important Note: 1. All statements and claims regarding turnover, operational and manufacturing experience and production capacity should be duly supported by authenticated copies of documents without which the tender is liable to be rejected summarily. PVVNL may call the tenderer to produce original purchase 	order / dispatch instruction or any other document for verification of submitted documents during the evaluation of their bid. The bidder is also required to submit an affidavit on stamp paper regarding the firm not being blacklisted by any government utility anywhere in India. If any information provided by the bidder is found to be concealed, supressed or incorrect at the later date, may lead to not only the cancellation of purchase order, if placed by on the tenderer, along with imposement of financial penalty and business debarment.

2.	 	In case applicant is a holding company, the Financial Position criteria / Operational & manufacturing experience criteria  referred in above clauses, shall be considered  that of holding company only (i.e. excluding its subsidiary / group companies ). In case applicant is a subsidiary of a holding company, the  Financial Position criteria / Operational & manufacturing experience criteria  referred in above clauses, shall be considered that of subsidiary company only (i.e. excluding its holding company)

Note:   PVVNL reserves the right to waive minor deviation if they do not materially affect the capability of the applicant to perform the contract.